## run info 04
name | English name | address | type of data | Number of bytes | data range | unit | remark | whether to store | modify | 0x03 | 0x04 | 0x06 | 0x10
Protocol header (model attribute information) | [7 empty] | Save this page to ARM |  | function code
inverter name | InverName | 0-5 | U16*6 | 12 | [5 empty] | X | √ | X | X
invertere type | InverType | 6 | U16 | 2 |  |  | 0-99 single phase inverter 100-199 three phase inverter 200-299 single phase hybrid inverter(including split phase inverter) 300-399 three phase hybrid inverter |  |  | X | √ | X | X
rated power | NormAppPower | 7-8 | U32 | 4 |  | 1W |  |  | 1. 1w 1VA; 1w changed into 1VA 2. 1VA 1W the rated apparent power was Revised to the rated power, unit: 1VA changed into 1W | X | √ | X | X
Rated output reactive power | NormReactPower | 9-10 | U32 | 4 |  | 1var |  |  |  | X | √ | X | X
hardware version | HardVer | 15 | U16 | 2 | [5 empty] | X | √ | X | X
protocol version | ProtocolVer | 20 | U16 | 2 |  |  | XXX.XX |  | start from 1 | X | √ | X | X
master DSP software version | MasterVer | 25 | U16 | 2 |  |  | XXX.XX |  |  | X | √ | X | X
slave DSP software version | SlaveVer | 30 | U16 | 2 |  |  | XXX.XX |  |  | X | √ | X | X
HMI Software version | HMIVer | 35 | U16 | 2 |  |  | XXX.XX |  |  | X | √ | X | X
CPLD Software version | CPLDVer | 40 | U16 | 2 |  |  | XXX.XX |  |  | X | √ | X | X
inverter SN | SerialNumber15-14 | 41 | U16 | 2 | ASCII |  |  |  |  | X | √ | X | X
| SerialNumber13-12 | 42 | U16 | 2 | ASCII |  |  |  |  | X | √ | X | X
| SerialNumber11-10 | 43 | U16 | 2 | ASCII |  |  |  |  | X | √ | X | X
| SerialNumber9-8 | 44 | U16 | 2 | ASCII |  |  |  |  | X | √ | X | X
| SerialNumber7-6 | 45 | U16 | 2 | ASCII |  |  |  |  | X | √ | X | X
| SerialNumber5-4 | 46 | U16 | 2 | ASCII |  |  |  |  | X | √ | X | X
| SerialNumber3-2 | 47 | U16 | 2 | ASCII |  |  |  |  | X | √ | X | X
| SerialNumber1-0 | 48 | U16 | 2 | ASCII |  |  |  |  | X | √ | X | X
country | Country | 49 | U16 | 2 | [5 empty] | X | √ | X | X
Max AC output current | MaxAcOutCurr | 50-51 | U32 | 4 |  | 0.01A |  |  | 0.01A newly added unit 0.01A | X | √ | X | X
inverter character | InverCharacter | 52-53 | U32 | 4 |  |  | B0-B2: 0 ；B0-B2: 0 refers to on grid inverter, 1 refers to low voltage hybrid inverter, 2 refers to high voltage hybrid inverter B3-B5: 0 ； B3-B5: 0 refers to single phase, 1 refers to split phase, 2 refers to three phase B6-B9: ； B6-B9: PV boost quantity, 0 means 1 channel, 1 means 2 channel, N means N+ channels B10: ； B11-B31：reserved； B10：0 means tranformerless, 1 means transformer, |  | the Newly added 21.05.12 is used to Platform identification, B1-B31 is changed into B11-B31 | X | √ | X | X
reserve | Reserve | 54-499 | [7 empty] | X | √ | X | X
Real-time operation information 1 (PV+ grid-connected operation information) | [9 empty] | X | √ | X | X
Bus voltage | Vbus | 500 | U16 | 2 |  | 0.1V | If it is single-phase, only R-phase voltage and R-phase current are valid; If it is two-phase, only R and S phase voltage and R and S phase current are valid; If three-phase four-wire system, it means: "X-phase voltage"; In the case of three-phase three-wire system, it means: "x-x line voltage". Positive means the inverter sends power to the grid, negative means the inverter draws power from the grid |  |  | X | √ | X | X
Negative bus voltage | Vnbus | 501 | U16 | 2 |  | 0.1V |  |  |  | X | √ | X | X
Insulation resistance value | Riso | 502 | U16 | 2 |  | KΩ |  |  |  | X | √ | X | X
Leakage current effective value | IgfciRms | 503 | U16 | 2 |  | 1mA |  |  |  | X | √ | X | X
DCI in R phase | DCIR | 504 | S16 | 2 |  | 1mA |  |  |  | X | √ | X | X
DCI in S phase | DCIS | 505 | S16 | 2 |  | 1mA |  |  |  | X | √ | X | X
DCI in T phase | DCIT | 506 | S16 | 2 |  | 1mA |  |  |  | X | √ | X | X
Grid Voltage in R phase | VgridR | 507 | U16 | 2 |  | 0.1V |  |  |  | X | √ | X | X
Grid Voltage in S phase | VgridS | 508 | U16 | 2 |  | 0.1V |  |  |  | X | √ | X | X
Grid Voltage in T phase | VgridT | 509 | U16 | 2 |  | 0.1V |  |  |  | X | √ | X | X
R phase inverter current | IinvR | 510 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
S phase inverter current | IinvS | 511 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
T phase inverter current | IinvT | 512 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
R phase grid frequency | FgridR | 513 | U16 | 2 |  | 0.01Hz |  |  |  | X | √ | X | X
S phase grid frequency | FgridS | 514 | U16 | 2 |  | 0.01Hz |  |  |  | X | √ | X | X
T phase grid frequency | FgridT | 515 | U16 | 2 |  | 0.01Hz |  |  |  | X | √ | X | X
A phase active power | PinvR | 516-517 | S32 | 4 |  | W |  |  |  | X | √ | X | X
B phase active power | PinvS | 518-519 | S32 | 4 |  | W |  |  |  | X | √ | X | X
C phase active power | PinvT | 520-521 | S32 | 4 |  | W |  |  |  | X | √ | X | X
Total active power | Pinv | 522-523 | S32 | 4 |  | W |  |  |  | X | √ | X | X
Total reactive power | Qinv | 524-525 | S32 | 4 |  | W |  |  |  | X | √ | X | X
Total power factor | PFinv | 526 | S16 | 2 |  | 0.001 |  |  |  | X | √ | X | X
Total apparent power | Sinv | 527-528 | U32 | 4 |  | VA |  |  |  | X | √ | X | X
R-phase grid-connected power (meter) | PgridR | 529-530 | S32 | 4 |  | W | Positive means the inverter sends power to the grid, negative means the inverter draws power from the grid |  |  | X | √ | X | X
S-phase grid-connected power (meter) | PgridS | 531-532 | S32 | 4 |  | W |  |  |  | X | √ | X | X
T-phase grid-connected power (meter) | PgridT | 533-534 | S32 | 4 |  | W |  |  |  | X | √ | X | X
Total grid-connected active power | Pgrid | 535-536 | S32 | 4 |  | W |  |  | newly added unit W | X | √ | X | X
Total grid-connected reactive power | Qgrid | 537-538 | S32 | 4 |  | Var |  |  | newly added unit Var | X | √ | X | X
Total grid-connected apparent power | Sgrid | 539-540 | U32 | 4 |  | VA |  |  | newly added unit VA | X | √ | X | X
Total load active power | Pload | 547-548 | S32 | 4 |  | W |  |  | newly added unit W | X | √ | X | X
PV total power | Ppv | 553-554 | U32 | 4 |  | W |  |  | newly added unit W | X | √ | X | X
PV1 voltage | Vpv1 | 555 | U16 | 2 |  | 0.1V |  |  |  | X | √ | X | X
PV1 current | Ipv1 | 556 | U16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
PV1 power | Ppv1 | 557 | U16 | 2 |  | W |  |  |  | X | √ | X | X
PV2 voltage | Vpv2 | 558 | U16 | 2 |  | 0.1V |  |  |  | X | √ | X | X
PV2 current | Ipv2 | 559 | U16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
PV2 power | Ppv2 | 560 | U16 | 2 |  | W |  |  |  | X | √ | X | X
PV3 voltage | Vpv3 | 561 | U16 | 2 |  | 0.1V |  |  |  | X | √ | X | X
PV3 current | Ipv3 | 562 | U16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
PV3 power | Ppv3 | 563 | U16 | 2 |  | W |  |  |  | X | √ | X | X
PV4 voltage | Vpv4 | 564 | U16 | 2 |  | 0.1V |  |  |  | X | √ | X | X
PV4 current | Ipv4 | 565 | U16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
PV4 power | Ppv4 | 566 | U16 | 2 |  | W |  |  |  | X | √ | X | X
reserve | Reserve | 567-999 | [7 empty] | X | √ | X | X
Real-time operation information 2 (PV + grid-connected power generation) | [9 empty] | X | √ | X | X
E-today | EInvOutDay | 1000 | U16 | 2 |  | 0.1kwh |  | YES | unit 0.1Wh changed into 0.1kWh | X | √ | X | X
Etoday received from grid by inverter | EInvRecDay | 1001 | U16 | 2 |  | 0.1kwh |  | YES |  | X | √ | X | X
Etoday feed into grid | EtogridDay | 1002 | U16 | 2 |  | 0.1kwh |  | YES |  | X | √ | X | X
Etoday received from grid | EfromgridDay | 1003 | U16 | 2 |  | 0.1kwh |  |  |  | X | √ | X | X
Etoday to load | EtoLoadDay | 1004 | U16 | 2 |  | 0.1kwh |  | YES |  | X | √ | X | X
Etoday from load | EfromLoadDay | 1005 | U16 | 2 |  | 0.1kwh |  |  |  | X | √ | X | X
PV Etoday | EPVDay | 1006-1007 | U32 | 4 |  | 0.1kwh |  | YES |  | X | √ | X | X
PV1 Etoday | EPV1Day | 1008 | U16 | 2 |  | 0.1kwh |  | YES |  | X | √ | X | X
PV2 Etoday | EPV2Day | 1009 | U16 | 2 |  | 0.1kwh |  | YES |  | X | √ | X | X
PV3 Etoday | EPV3Day | 1010 | U16 | 2 |  | 0.1kwh |  | YES |  | X | √ | X | X
PV4 Etoday | EPV4Day | 1011 | U16 | 2 |  | 0.1kwh |  | YES |  | X | √ | X | X
Etotal by inverter | EInvOutTotal | 1014-1015 | U32 | 4 |  | 0.1kwh |  | YES |  | X | √ | X | X
Etotal received by inverter from grid | EInvRecTotal | 1016-1017 | U32 | 4 |  | 0.1kwh |  | YES |  | X | √ | X | X
Etotal feed into grid | EtogridTotal | 1018-1019 | U32 | 4 |  | 0.1kwh |  | YES |  | X | √ | X | X
Etotal received from grid | EfromgridTotal | 1020-1021 | U32 | 4 |  | 0.1kwh |  |  |  | X | √ | X | X
Etotal to load | EtoLoadTotal | 1022-1023 | U32 | 4 |  | 0.1kwh |  | YES |  | X | √ | X | X
Reserve | Reserve | 1028-1499 | [7 empty] | X | √ | X | X
Real-time operation information 5 (system information) | [9 empty] | X | √ | X | X
Run status | RunState | 2500 | U16 | 2 |  |  | Initial power-up 0 standby 1 start up 2 run grid connected 3 run grid disconnected 4 run generator 5 switch from on grid connected to off grid 6 switch from off grid connected to on grid 7 Power-down processing 8 turn off 9 error 10 update 11 aging 12 Open loop 13 Sampling calibration 14 |  |  | X | √ | X | X
Inverter inner temperature | Tinner | 2514 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
transformer temperature | Ttransf | 2515 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
Real-time operation information 6 (faults and alarms) | [9 empty] | X | √ | X | X
PV error 1 | PvErr1 | 3000-3001 | U32 | 4 | [5 empty] | X | √ | X | X
PV error 2 | PvErr2 | 3002-3003 | U32 | 4 | [5 empty] | X | √ | X | X
grid error | GridErr | 3008-3009 | U32 | 4 | [5 empty] | X | √ | X | X
off grid error | OffGridErr | 3010-3011 | U32 | 4 | [5 empty] | X | √ | X | X
DC side error 1 | DCErr1 | 3012-3013 | U32 | 4 | [5 empty] | X | √ | X | X
DC side error 2 | DCErr2 | 3014-3015 | U32 | 4 | [5 empty] | X | √ | X | X
AC side error | ACErr | 3016-3017 | U32 | 4 | [5 empty] | X | √ | X | X
system error1 | SysErr1 | 3018-3019 | U32 | 4 | [5 empty] | X | √ | X | X
system error2 | SysErr2 | 3020-3021 | U32 | 4 | [5 empty] | X | √ | X | X
permanent error | PermErr | 3022-3023 | U32 | 4 | [5 empty] | X | √ | X | X
innver warming | InWarning | 3024-3025 | U32 | 4 | [5 empty] | X | √ | X | X
outer warming | OutWarning | 3026-3027 | U32 | 4 | [5 empty] | X | √ | X | X
reserve | Reserve | 3028-3499 | [7 empty] | X | √ | X | X

## Read and Write parametr03-06-10
name | English | add | type of data | Number of bytes | data range | unit | remark | flash Whether store to external flash | modify | Variable name | 0x03 | 0x04 | 0x06 | 0x10
set parameter 1(system parameter) | [10 empty] | unction code
Rated active power | NormActPower | 200-201 | U32 | 4 | [5 empty] | gulDeNormActPwr | √ | X | √ | √
Rated apparent power | NormAppPower | 202-203 | U32 | 4 | [5 empty] | gulDeNormAppPwr | √ | X | √ | √
country choose | Country | 204 | U16 | 2 | country |  | The inverter needs to be restarted after setting | yes |  | guwDeSafty | √ | X | √ | √
PV input mode | PVInputType | 205 | U16 | 2 |  |  | 0: alone 1: in parallel 2: no PV | yes | newly added 2: no PV | guwDePvInputType | √ | X | √ | √
Run function enable | FuncEn | 206-207 | U32 | 4 |  |  | B0: turn on/off inverter B1:Soft start enable B2~B7 reserved B8:DRMS enable B9:ripple control B10: Power drop when high grid voltage B11: Power increase when low grid voltage B12: Power drop when high grid frequency B13: Power increase when low grid frequency B14:HVRT B15:LVRT B16~B31 Reseved | yes | 1. B5与B6调换位置，修改B16为Forbid discharge enable，移除B17。 2. “AC charge enable”修改为“Timing AC charge enable” “Forced charge enable”修改为“Timing charge enable” “Forced discharge enable”修改为“Timing discharge enable” “Forbid discharge enable”修改为“Timing Forbid discharge enable” | gulDeSysFuncEn | √ | X | √ | √
PV start up voltage | PvStartVolt | 210 | U16 | 2 |  | 0.1V |  | yes |  | guwDeStartVpv | √ | X | √ | √
CT or Meter | MeterType | 211 | U16 | 2 | 0：no merter 1：CT 2：meter |  |  | yes |  | guwDeMeterType | √ | X | √ | √
smart meter factory | MeterBrand | 212 | U16 | 2 | 1： 2： |  |  | yes |  | guwDeMeterBrand | √ | X | √ | √
set parameter 2(system order) | [10 empty] | √ | X | √ | √
time | TimeYear-Month | 500 | U16 | 2 | H:18-99 L:1-12 |  |  | No |  | guwDeSysTYearMonth | √ | X | √ | √
| TimeDate-Hour | 501 | U16 | 2 | H:1-31 L:0-23 |  |  | No |  | guwDeSysTDateHour | √ | X | √ | √
| TimeMinute-Sec | 502 | U16 | 2 | H:0-59 L:0-59 |  |  | No |  | guwDeSysTMinuteSec | √ | X | √ | √
Update enable | UpdataEn | 521 | U16 | 2 |  |  | 0xAA valid | No |  | guwDeUpdataEn | √ | X | X | √
Upgrade baud rate | UpdataBaud | 522 | U16 | 2 |  |  | 0: 9600 1: 115200 | No |  | guwDeUpdataBaud | √ | X | X | √
update which software | UpdataCpuNum | 523 | U16 | 2 |  |  | 1：HMI(display board) 2: Master(DSP) 3: Slave(DSP) | No |  | guwDeUpdataCpuNum | √ | X | X | √
| UpdataPackSize (updated software pack size) | 524 | U16 | 2 |  |  |  | No |  | guwDeUpdataPackSize | √ | X | X | √
set parameter 3(protect parameter) | [10 empty] | √ | X | √ | √
Grid-connected condition judgment time | GridOnJudgTime | 1000 | U16 | 2 | 10-1200 | S |  | yes |  | guwDeGridOnJudgT | √ | X | √ | √
Grid-connected maximum allowable voltage | GridOnVoltMax | 1001 | U16 | 2 | 1010-3200 | 0.1V |  | yes |  | guwDeGridOnVMax | √ | X | √ | √
Grid-connected min allowable voltage | GridOnVoltMin | 1002 | U16 | 2 | 500-2300 | 0.1V |  | yes |  | guwDeGridOnVMin | √ | X | √ | √
Grid-connected max allowable frequency | GridOnFreqMax | 1003 | U16 | 2 | 5000-7000 | 0.01Hz |  | yes |  | guwDeGridOnFMax | √ | X | √ | √
Grid-connected min allowable frequency | GridOnFreqMin | 1004 | U16 | 2 | 4000-6000 |  |  | yes |  | guwDeGridOnFMin | √ | X | √ | √
Grid overvoltage recovery point | GridVoltMaxRecover | 1007 | U16 | 2 | 1010-3200 | 0.1V |  | yes |  | guwDeGridVMaxRec | √ | X | √ | √
Grid under-voltage recovery point | GridVoltMinRecover | 1008 | U16 | 2 | 500-2300 | 0.1V |  | yes |  | guwDeGridVMinRec | √ | X | √ | √
Grid over-frequency recovery point | GridFreqMaxRecover | 1009 | U16 | 2 | 5000-7000 | 0.01Hz |  | yes |  | guwDeGridFMaxRec | √ | X | √ | √
Grid under-frequency recovery point | GridFreqMinRecover | 1010 | U16 | 2 | 4000-6000 | 0.01Hz |  | yes |  | guwDeGridFMinRec | √ | X | √ | √
Grid overvoltage level 1 protection value (Default single level) | GridVoltMax1 | 1011 | U16 | 2 | 1000-4000 | 0.1V |  | yes |  | guwDeGridVMax1 | √ | X | √ | √
Grid overvoltage level 1 protection time (Default single level) | GridVoltMaxTime1 | 1012 | U16 | 2 | 0-30000 (all protection) | 0.01S |  | yes |  | guwDeGridVMaxTime1 | √ | X | √ | √
Grid under-frequency level 1 protection value (Default single level) | GridVoltMin1 | 1013 | U16 | 2 | 500-2500 | 0.1V |  | yes |  | guwDeGridVMin1 | √ | X | √ | √
Grid under-frequency level 1 protection time (Default single level) | GridVoltMinTime1 | 1014 | U16 | 2 | 0-30000(all protection) | 0.01S |  | yes |  | guwDeGridVMinTime1 | √ | X | √ | √
Grid overvoltage level 2 protection value | GridVoltMax2 | 1015 | U16 | 2 | 1000-4000 | 0.1V |  | yes |  | guwDeGridVMax2 | √ | X | √ | √
Grid overvoltage level 2 protection time | GridVoltMaxTime2 | 1016 | U16 | 2 | 0-30000(all protection) | 0.01S |  | yes |  | guwDeGridVMaxTime2 | √ | X | √ | √
Grid under-voltage level 2 protection value | GridVoltMin2 | 1017 | U16 | 2 | 500-2500 | 0.1V |  | yes |  | guwDeGridVMin2 | √ | X | √ | √
Grid under-voltage level 2 protection time | GridVoltMinTime2 | 1018 | U16 | 2 | 0-30000(all protection) | 0.01S |  | yes |  | guwDeGridVMinTime2 | √ | X | √ | √
Grid over-frequency level 1 protection value(Default single level) | GridFreqMax1 | 1031 | U16 | 2 | 5000-7000 | 0.01Hz |  | yes |  | guwDeGridFMax1 | √ | X | √ | √
Grid over-frequency level 1 protection time (Default single level) | GridFreqMaxTime1 | 1032 | U16 | 2 | 0-30000(all protection) | 0.01S |  | yes |  | guwDeGridFMaxTime1 | √ | X | √ | √
Grid under-frequency level 1 protection value (Default single level) | GridFreqMin1 | 1033 | U16 | 2 | 4000-6000 | 0.01Hz |  | yes |  | guwDeGridFMin1 | √ | X | √ | √
Grid under-frequency level 1 protection time (Default single level) | GridFreqMinTime1 | 1034 | U16 | 2 | 0-30000(all protection) | 0.01S |  | yes |  | guwDeGridFMinTime1 | √ | X | √ | √
Grid over-frequency level 2 protection value | GridFreqMax2 | 1035 | U16 | 2 | 5000-7000 | 0.01Hz |  | yes |  | guwDeGridFMax2 | √ | X | √ | √
Grid over-frequency level 2 protection time | GridFreqMaxTime2 | 1036 | U16 | 2 | 0-30000(所有保护all protection) | 0.01S |  | yes |  | guwDeGridFMaxTime2 | √ | X | √ | √
Grid under-frequency level 2 protection value | GridFreqMin2 | 1037 | U16 | 2 | 4000-6000 | 0.01Hz |  | yes |  | guwDeGridFMin2 | √ | X | √ | √
Grid under-frequency level 2 protection time | GridFreqMinTime2 | 1038 | U16 | 2 | 0-30000(all protection) | 0.01S |  | yes |  | guwDeGridFMinTime2 | √ | X | √ | √
Insulation resistance lower limit | IsoResMin | 1053 | U16 | 2 | 10-800 | KΩ |  | yes |  | guwDeIsoResMin | √ | X | √ | √
DCI upper limit | DcIMax | 1054 | U16 | 2 | 20-2000 | mA |  | yes |  | guwDeDcIMax | √ | X | √ | √
Setting parameter 4 (Grid dispatching parameter 1) | [10 empty] | √ | X | √ | √
Reactive power threshold | NormReactPower | 1500-1501 | U32 | 4 | 0-200000 | VA |  | yes |  | glDeNormReactPwr | √ | X | √ | √
Active output power limit | OutPwrMaxPer | 1502 | U16 | 2 | 0-1000 | 0.1% |  | yes |  | guwDeOutPwrMaxPer | √ | X | √ | √
Maximum active output power | OutPwrMax | 1503-1504 | U32 | 4 | 0-200000 | W |  | yes |  | gulDeOutPwrMax | √ | X | √ | √
Over-frequency derating curve | PbyFOverCurve | 1505 | U16 | 2 |  |  |  | yes |  | guwDePbyFOverCurve | √ | X | √ | √
Over-frequency derating F1 | PbyFOverF1 | 1506 | U16 | 2 | 5000-7000 | 0.01Hz |  | yes |  | guwDePbyFOverF1 | √ | X | √ | √
Over-frequency derating F2 | PbyFOverF2 | 1507 | U16 | 2 | 5000-7000 | 0.01Hz |  | yes |  | guwDePbyFOverF2 | √ | X | √ | √
Over-frequency derating F3 | PbyFOverF3 | 1508 | U16 | 2 | 5000-7000 | 0.01Hz |  | yes |  | guwDePbyFOverF3 | √ | X | √ | √
Over-frequency derating F4 | PbyFOverF4 | 1509 | U16 | 2 | 5000-7000 | 0.01Hz |  | yes |  | guwDePbyFOverF4 | √ | X | √ | √
Over-frequency derating P1 | PbyFOverP1 | 1510 | S16 | 2 | 0-2000 | 0.1% |  | yes |  | gwDePbyFOverP1 | √ | X | √ | √
Over-frequency derating P2 | PbyFOverP2 | 1511 | S16 | 2 | 0-2000 | 0.1% |  | yes |  | gwDePbyFOverP2 | √ | X | √ | √
Over-frequency derating P3 | PbyFOverP3 | 1512 | S16 | 2 | 0-2000 | 0.1% |  | yes |  | gwDePbyFOverP3 | √ | X | √ | √
Over-frequency derating P4 | PbyFOverP4 | 1513 | S16 | 2 | 0-2000 | 0.1% |  | yes |  | gwDePbyFOverP4 | √ | X | √ | √
Over-frequency derating recovery point | PbyFOverFRecover | 1514 | U16 | 2 | 5000-7000 | 0.01Hz |  | yes |  | guwDePbyFOverFRecover | √ | X | √ | √
Active power derating rate during over-frequency derating | PbyFOverRate | 1515 | U16 | 2 | 0-5000 | 0.1%/Hz |  | yes |  | guwDePbyFOverRate | √ | X | √ | √
Waiting for recovery time after over-frequency derating | PbyFOverTRecover | 1516 | U16 | 2 |  |  |  | yes |  | guwDePbyFOverTRecover | √ | X | √ | √
Active power recovery rate after over-frequency derating | PbyFOverRateRecover | 1517 | U16 | 2 |  |  |  | yes |  | guwDePbyFOverRateRecover | √ | X | √ | √
Over-frequency derating response time | PbyFOverT | 1518 | U16 | 2 |  |  |  | yes |  | guwDePbyFOverT | √ | X | √ | √
Under-frequency upscaling curve | PbyFRiseCurve | 1519 | U16 | 2 |  |  |  | yes |  | guwDePbyFRiseCurve | √ | X | √ | √
Under-frequency rise F1 | PbyFRiseF1 | 1520 | U16 | 2 | 4000-6000 | 0.01Hz |  | yes |  | guwDePbyFRiseF1 | √ | X | √ | √
Under-frequency rise F2 | PbyFRiseF2 | 1521 | U16 | 2 | 4000-6000 | 0.01Hz |  | yes |  | guwDePbyFRiseF2 | √ | X | √ | √
Under-frequency rise F3 | PbyFRiseF3 | 1522 | U16 | 2 | 4000-6000 | 0.01Hz |  | yes |  | guwDePbyFRiseF3 | √ | X | √ | √
Under-frequency rise F4 | PbyFRiseF4 | 1523 | U16 | 2 | 4000-6000 | 0.01Hz |  | yes |  | guwDePbyFRiseF4 | √ | X | √ | √
Under-frequency rise P1 | PbyFRiseP1 | 1524 | S16 | 2 | 0-2000 | 0.1% |  | yes |  | gwDePbyFRiseP1 | √ | X | √ | √
Under-frequency rise P2 | PbyFRiseP2 | 1525 | S16 | 2 | 0-2000 | 0.1% |  | yes |  | gwDePbyFRiseP2 | √ | X | √ | √
Under-frequency rise P3 | PbyFRiseP3 | 1526 | S16 | 2 | 0-2000 | 0.1% |  | yes |  | gwDePbyFRiseP3 | √ | X | √ | √
Under-frequency rise P4 | PbyFRiseP4 | 1527 | S16 | 2 | 0-2000 | 0.1% |  | yes |  | gwDePbyFRiseP4 | √ | X | √ | √
Under-frequency up-rate recovery point | PbyFRiseFRecover | 1528 | U16 | 2 | 4000-6000 | 0.01Hz |  | yes |  | guwDePbyFRiseFRecover | √ | X | √ | √
Active power increase rate during under-frequency increase | PbyFRiseRate | 1529 | U16 | 2 | 0-5000 | 0.1%/Hz |  | yes |  | guwDePbyFRiseRate | √ | X | √ | √
Waiting for recovery time after underfrequency upscaling | PbyFRiseTRecover | 1530 | U16 | 2 |  |  |  | yes |  | guwDePbyFRiseTRecover | √ | X | √ | √
Active power recovery rate after under-frequency increase | PbyFRiseRateRecover | 1531 | U16 | 2 |  |  |  | yes |  | guwDePbyFRiseRateRecover | √ | X | √ | √
Response time for under-frequency upscaling | PbyFRiseT | 1532 | U16 | 2 |  |  |  | yes |  | guwDePbyFRiseT | √ | X | √ | √
Grid overvoltage power regulation voltage 1 | PbyVOverV1 | 1533 | U16 | 2 | 1000-4000 | 0.1V |  | yes |  | guwDePbyVOverV1 | √ | X | √ | √
Grid overvoltage power regulation voltage 1 | PbyVOverV2 | 1534 | U16 | 2 | 1000-4000 | 0.1V |  | yes |  | guwDePbyVOverV2 | √ | X | √ | √
Grid overvoltage power regulation voltage 1 | PbyVOverV3 | 1535 | U16 | 2 | 1000-4000 | 0.1V |  | yes |  | guwDePbyVOverV3 | √ | X | √ | √
Grid overvoltage power regulation voltage 1 | PbyVOverV4 | 1536 | U16 | 2 | 1000-4000 | 0.1V |  | yes |  | guwDePbyVOverV4 | √ | X | √ | √
Grid overvoltage power regulation power 1 | PbyVOverP1 | 1537 | S16 | 2 | 0-2000 | 0.1% |  | yes |  | gwDePbyVOverP1 | √ | X | √ | √
Grid overvoltage power regulation power 2 | PbyVOverP2 | 1538 | S16 | 2 | 0-2000 | 0.1% |  | yes |  | gwDePbyVOverP2 | √ | X | √ | √
Grid overvoltage power regulation power 3 | PbyVOverP3 | 1539 | S16 | 2 | 0-2000 | 0.1% |  | yes |  | gwDePbyVOverP3 | √ | X | √ | √
Grid overvoltage power regulation power 4 | PbyVOverP4 | 1540 | S16 | 2 | 0-2000 | 0.1% |  | yes |  | gwDePbyVOverP4 | √ | X | √ | √
Grid overvoltage power regulation time | PbyVOverT | 1541 | U16 | 2 | 0-30000 | 0.01s |  | yes |  | guwDePbyVOverT | √ | X | √ | √
Grid undervoltage power regulation voltage 1 | PbyVUnderV1 | 1542 | U16 | 2 | 500-2500 | 0.1V |  | yes |  | guwDePbyVUnderV1 | √ | X | √ | √
Grid undervoltage power regulation voltage 2 | PbyVUnderV2 | 1543 | U16 | 2 | 500-2500 | 0.1V |  | yes |  | guwDePbyVUnderV2 | √ | X | √ | √
Grid undervoltage power regulation voltage 3 | PbyVUnderV3 | 1544 | U16 | 2 | 500-2500 | 0.1V |  | yes |  | guwDePbyVUnderV3 | √ | X | √ | √
Grid undervoltage power regulation voltage 4 | PbyVUnderV4 | 1545 | U16 | 2 | 500-2500 | 0.1V |  | yes |  | guwDePbyVUnderV4 | √ | X | √ | √
Grid undervoltage power regulation power 1 | PbyVUnderP1 | 1546 | S16 | 2 | 0-2000 | 0.1% |  | yes |  | gwDePbyVUnderP1 | √ | X | √ | √
Grid undervoltage power regulation power 2 | PbyVUnderP2 | 1547 | S16 | 2 | 0-2000 | 0.1% |  | yes |  | gwDePbyVUnderP2 | √ | X | √ | √
Grid undervoltage power regulation power 3 | PbyVUnderP3 | 1548 | S16 | 2 | 0-2000 | 0.1% |  | yes |  | gwDePbyVUnderP3 | √ | X | √ | √
Grid undervoltage power regulation power 4 | PbyVUnderP4 | 1549 | S16 | 2 | 0-2000 | 0.1% |  | yes |  | gwDePbyVUnderP4 | √ | X | √ | √
Grid undervoltage power regulation time | PbyVUnderT | 1550 | U16 | 2 | 0-30000 | 0.01s |  | yes |  | guwDePbyVUnderT | √ | X | √ | √
reactive power control | QMode | 1551 | U16 | 2 |  |  | 0：Normal 1：Q Set(P1518) 2：Pf Set(P1519) 3：Q By V(P1520~1525) 4：Pf By P(P1526~1527) | yes |  | guwDeQMode | √ | X | √ | √
reactive power set 100% | QSet% | 1552 | S16 | 2 | (-1000~1000) | 0.001 |  |  |  | gwDeQPerSet | √ | X | √ | √
reactive power set | QSet | 1553-1554 | S32 | 4 | ‘-200000~200000 | VA |  | yes |  | glDeQSet | √ | X | √ | √
PF set | PfSet | 1555 | S16 | 2 | (-1000~-800,800~1000) | 0.001 | V1<V2<V3<V4 | yes |  | gwDePfSet | √ | X | √ | √
QByV_V1 | QByVV1 | 1556 | U16 | 2 | 800-1000 | 0.1% |  |  |  | guwDeQByVV1 | √ | X | √ | √
QByV_V2 | QByVV2 | 1557 | U16 | 2 | 800-1000 | 0.1% |  |  |  | guwDeQByVV2 | √ | X | √ | √
QByV_V3 | QByVV3 | 1558 | U16 | 2 | 1000-1100 | 0.1% |  |  |  | guwDeQByVV3 | √ | X | √ | √
QByV_V4 | QByVV4 | 1559 | U16 | 2 | 1000-1200 | 0.1% |  |  |  | guwDeQByVV4 | √ | X | √ | √
QByV_Pct1 | QByVQ1 | 1560 | S16 | 2 | 0-40 | 0.1% |  | yes |  | gwDeQByVQ1 | √ | X | √ | √
QByV_Pct2 | QByVQ2 | 1561 | S16 | 2 | [5 empty] | gwDeQByVQ2 | √ | X | √ | √
QByV_Pct3 | QByVQ3 | 1562 | S16 | 2 | [5 empty] | gwDeQByVQ3 | √ | X | √ | √
QByV_Pct4 | QByVQ4 | 1563 | S16 | 2 | -40-0 | 0.1% |  | yes |  | gwDeQByVQ4 | √ | X | √ | √
PfByPPStart | PfByPPStart | 1564 | S16 | 2 | 40-100 | 0.1% |  | yes |  | gwDePfByPPStart | √ | X | √ | √
PfByPPfEnd | PfByPPfEnd | 1565 | S16 | 2 | (-1000~-800,800~1000) | 0.001 |  | yes |  | gwDePfByPPfEnd | √ | X | √ | √
PfByPRate | PfByPRate | 1566 | U16 | 2 | 0-5000 | 0.1%Hz |  |  |  | guwDePfByPRate | √ | X | √ | √
PfByP_P1 | PfByPP1 | 1567 | S16 | 2 | -1000-+1000 | 0.1% |  |  |  | gwDePfByPP1 | √ | X | √ | √
PfByP_P2 | PfByPP2 | 1568 | S16 | 2 | -1000-+1000 | 0.1% |  |  |  | gwDePfByPP2 | √ | X | √ | √
PfByP_P3 | PfByPP3 | 1569 | S16 | 2 | -1000-+1000 | 0.1% |  |  |  | gwDePfByPP3 | √ | X | √ | √
PfByP_P4 | PfByPP4 | 1570 | S16 | 2 | -1000-+1000 | 0.1% |  |  |  | gwDePfByPP4 | √ | X | √ | √
PfByP_Pf1 | PfByPPf1 | 1571 | S16 | 2 | -100--1000, +100-+1000 | 0.1% |  |  |  | gwDePfByPPf1 | √ | X | √ | √
PfByP_Pf2 | PfByPPf2 | 1572 | S16 | 2 | -100--1000, +100-+1000 | 0.1% |  |  |  | gwDePfByPPf2 | √ | X | √ | √
PfByP_Pf3 | PfByPPf3 | 1573 | S16 | 2 | -100--1000, +100-+1000 | 0.1% |  |  |  | gwDePfByPPf3 | √ | X | √ | √
PfByP_Pf4 | PfByPPf4 | 1574 | S16 | 2 | -100--1000, +100-+1000 | 0.1% |  |  |  | gwDePfByPPf4 | √ | X | √ | √
Q(P) function enable voltage proportional point | PfByPEnV | 1575 | U16 | 2 |  |  |  | yes |  | guwDePfByPEnV | √ | X | √ | √
The voltage proportional point at which the Q(P) function exits enable | PfByPDisV | 1576 | U16 | 2 |  |  |  | yes |  | guwDePfByPDisV | √ | X | √ | √
The power proportional point at which the Q(P) function exits enable | PfByPDisP | 1577 | S16 | 2 |  |  |  | yes |  | gwDePfByPDisP | √ | X | √ | √
Q(U) function enable power ratio point | QByVEnP | 1578 | S16 | 2 |  |  |  | yes |  | gwDeQByVEnP | √ | X | √ | √
Q(U) function exit enable power ratio point | QByVDisP | 1579 | S16 | 2 |  |  |  | yes |  | gwDeQByVDisP | √ | X | √ | √
set parameter 5(Power grid dispatching parameters 2) | [10 empty] | √ | X | √ | √
Initial grid-connection time | IniConnecT | 2037 | U16 | 2 | [5 empty] | guwDeIniConnecT | √ | X | √ | √
Fault reconnection time | ReConnecT | 2038 | U16 | 2 | 20-600 | S |  | yes |  | guwDeReConnecT | √ | X | √ | √
limit value of feed into grid power | GridFeedPlimit | 2039-2040 | S32 | 4 | 0-1000 | 0.1% |  | yes |  | glDeGridFeedPlimit | √ | X | √ | √

## National Safety Reg
国家 | 编码 | 备注 | The value of the register address (10 hex) | Country | country | Remark
Com_50Hz | 0 | 50Hz宽范围参数 | 0 | Com_50Hz | 50Hz Wide range of parameters
Com_60Hz | 1 | 60Hz宽范围参数 | 1 | Com_60Hz | 60Hz Wide range of parameters
CN | 2 | 中国 | 2 | CN | China
JP_50Hz | 3 | 日本50Hz电网 | 3 | JP_50Hz | Japan 50Hz Grid
JP_60Hz | 4 | 日本60Hz电网 | 4 | JP_60Hz | Japan 60Hz Grid
US_240S | 5 | 美国240V单相 | 5 | US_240S | US 240v single phase
US_240D | 6 | 美国240V裂相 | 6 | US_240D | US 240v split phase
US_208S | 7 | 美国208V单相 | 7 | US_208S | US 208v single phase
US_208D | 8 | 美国208V裂相 | 8 | US_208D | US 208v split phase
AU | 9 | 澳大利亚 | 9 | AU | Australia
UK_G98 | 10 | 英国G98标准 | 10 | UK_G98 | England G98 standard
UK_G99 | 11 | 英国G99标准 | 11 | UK_G99 | England G99 standard
DE | 12 | 德国低压电网 | 12 | DE | Germany low voltage grid
DE_BDEW | 13 | 德国中压电网 | 13 | DE_BDEW | Germany middle voltage grid
FR | 14 | 法国 | 14 | FR | France
FR_IL50Hz | 15 | 法国50Hz岛屿 | 15 | FR_IL50Hz | French 50Hz islands
FR_IL60Hz | 16 | 法国60Hz岛屿 | 16 | FR_IL60Hz | French 60Hz islands
PL | 17 | 波兰 | 17 | PL | Poland
IT | 18 | 意大利 | 18 | IT | Italy
TH_ME | 19 | 泰国ME地区 | 19 | TH_ME | Thai ME Area
TH_PE | 20 | 泰国PE地区 | 20 | TH_PE | Thai PE Area
IN | 21 | 印度 | 21 | IN | India
KR | 22 | 韩国 | 22 | KR | South korea
PH | 23 | 菲律宾 | 23 | PH | Philippine
KP | 24 | 朝鲜 | 24 | KP | North Korea
MY | 25 | 马来西亚 | 25 | MY | Malaysia
CY | 26 | 塞浦路斯 | 26 | CY | Cyprus
NL | 27 | 荷兰 | 27 | NL | Netherland
NL_16A | 28 | 荷兰限制16A并网 | 28 | EU | EU EN50549-1 Standard
ES | 29 | 西班牙 | 29 | ES | Spain
GR | 30 | 希腊 | 30 | GR | Greece
GR_IL | 31 | 希腊岛屿 | 31 | GR_IL | Greece island | reserve
PT | 32 | 葡萄牙 | 32 | PT | Portugal
BE | 33 | 比利时 | 33 | BE | Belgium
DK | 34 | 丹麦 | 34 | DK | Denmark
DK_16A | 35 | 丹麦限制16A并网 | 35 | DK_16A | Denmark restricts 16A grid connection | reserve
CZ | 36 | 捷克 | 36 | CZ | Czech Republic | reserve
SK | 37 | 斯洛伐克 | 37 | SK | Slovakia | reserve
SE | 38 | 瑞典 | 38 | SE | Sweden
AT | 39 | 奥地利 | 39 | AT | Austria | reserve
BG | 40 | 保加利亚 | 40 | BG | Bulgaria | reserve
RO | 41 | 罗马尼亚 | 41 | RO | Romania | reserve
UA | 42 | 乌克兰 | 42 | UA | Ukraine
ZA | 43 | 南非 | 43 | ZA | South Africa
MU | 44 | 毛里求斯 | 44 | MU | Mauritius
IL | 45 | 以色列 | 45 | IL | Israel
MX | 46 | 墨西哥 | 46 | MX | Mexico
BR | 47 | 巴西 | 47 | BR | Brazil
LK | 48 | 斯里兰卡 | 48 | LK | Sri Lanka
CL | 49 | 智利 | 49 | CL | Chile
CONNERA | 50 | 墨西哥CONNERA定制 | 50 | CONNERA | Mexico CONNERA custom
EU | 51 | 欧盟EN50549-1标准