## first page
Protocol Change Record
No. | Version | Date | Communication Protocol Modification | signature
1 | V1.00 | 2022-07-06 | Original version | Simon
2 | V1.00 | 2022-08-25 | 1,The power percentage is modified to 1%Pn unit; The loading rate is maintained at 0.1%Pn/min | Simon
3 | V1.00 | 2022-09-06 | Add Holding register 136/137 to define charge and discharge power in load priority | Simon
5 | V1.02 | 2023-01-30 | Add remote power mode regulation and slope definition regulation to the holding register 71~72 (German safety regulations) | Simon
6 | V1.03 | 2023-03-24 | Add Qmin parameters to the holding register 110 | Simon
7 | V1.04 | 2023-06-28 | Data type description and parameter description modification are added to the Input register data | Simon、朱毅
8 | V1.04 | 2023-07-10 | Add holding register 289 parameter, voltage active power stabilization time | Simon
10 | V1.06 | 2023-09-20 | Add input320~328 for Autotest parameter passing of Italian safety | Simon
12 | V1.08 | 2023-10-13 | Add bypass status to the comment of Input register 0 | 丁志鑫
13 | V1.09 | 2023-11-01 | Add 220V setting option to the holding register 88 | 朱毅
14 | V1.10 | 2023-11-06 | The Bus unbalanced current parameter is added to Input register 117 | 陈湘宁
15 | V1.11 | 2023-11-22 | The parallel mode of inverter AC output is added to holding register 119 | 丁志鑫
16 | V1.12 | 2023-11-27 | The battery protocol description is modified in the holding register 82 | 陈湘宁
16 | V1.13 | 2023-12-01 | Add the generator voltage to Input register 108. | 丁志鑫
17 | V1.14 | 2023-12-07 | Generator voltage is added to Input Register 118 and CT detection is added to Input Register 119. | 丁志鑫
18 | V1.15 | 2023-12-08 | 1、Add SOC setting points such as heat pump to holding register 233. 2、Add external wifi switch control status bit to Input Register120. | 朱毅
19 | V1.16 | 2023-12-08 | 1、 The holding registers 233~235 were modified to set the SOC start point of the heat pump. 2、Holding register 236 is added for setting the switching mode of heat pump. 3、The Input register 120 is modified for the heat pump switch status bit. | 陈成鑫
20 | V1.17 | 2023-12-14 | Holding register 79 is added for setting the AC Couple | 朱毅
21 | V1.18 | 2023-12-28 | 1、The holding register68 is added for PV power percentage limit setting; | 朱毅
22 | V1.19 | 2024-01-03 | 1.Input register 5,10,15,20 are deleted. PV current uses only one register. 2.The unit of holding register 68 is changed to 1 3.The safety number range of holding register 94 is changed to 0 to 255 | 丁志鑫
22 | V1.20 | 2024-01-05 | 1.Add active power percentage starting point of the default PF curve, reactive power Q2 of the undervoltage starting point of the Q(v) curve, and reactive power Q3 of the overvoltage starting point of the Q(v) curve to the holding registers 120, 121,and 122 respectively 2.Add active power loading rate, power at starting point of undervoltage derating, and power at starting point of overvoltage derating to holding registers 280,290 and 291 respectively | 朱毅
23 | V1.21 | 2024-01-05 | 1.The holding register 111 is added as the island enable setting 2.The holding register 112 is added as DRMS enable setting | 朱毅
24 | V1.22 | 2024-01-05 | 1.The holding register 80 is added to the anti-reverse current enable setting for hardware | 朱毅
25 | V1.23 | 2024-01-06 | 1.The input register 121 is added for software subversion display | 朱毅
26 | V1.24 | 2024-01-08 | 1.The input register 193 is added as the cutoff discharge voltage of the lithium battery | 陈湘宁
27 | V1.25 | 2024-01-08 | 1.The input register 149 and 150 is added as battery power | 丁志鑫
28 | V1.26 | 2024-01-16 | 1.Add logical interface flag to input register 329 | 陈湘宁
30 | V1.28 | 2024-01-17 | 1.Add cutoff SOC for period 1-20 to holding register 327-346 | 丁志鑫
31 | V1.29 | 2024-01-19 | 1.Delete Holding register 249 2. Holding register 81 (N-PE Enable) and Holding register 93 (H-LVRT Enable) are added 3、Deactivate the Holding register 32 (system safety enablement bit) | 朱毅
32 | V1.30 | 2024-01-22 | 1、Add three battery fault and three battery warning messages to input register 194~199 2、Add slave machines version information to input register 200~204 | 莫细红
32 | V1.31 | 2024-02-01 | 1、Off-grid constant power enable is added to Holding register 108 | 陈湘宁
33 | V1.32 | 2024/2/19日 | 1、Change the ratio of the anti-reverse power percentage in holding register 75: 1%->0.1% | 陈湘宁
33 | V1.32 | 2024/2/19日 | 1、Change the ratio of the anti-reverse current failure power percentage in holding register 78: 1%->0.1% | 陈湘宁
34 | V1.33 | 2024-02-23 | 1. Add comments to multiple input registers (23-28,29-36,38-44,46-52,60-77,81-84,87-90,93-96,98-101) to make their meaning clearer 2. Change the name of the input register (33-34) to make it more accurately expressed 3.The unused 108-109 registers are deleted, making them reserved registers 4.Parameters related to AC-Couple meter power are added to the input registers (330-335)
35 | V1.34 | 2024-04-05 | 1、Add parallel parameters to input register 336-338 | 莫细红
36 | V1.35 | 2024-04-09 | The Holding register88 modifies the value range and type of off-grid voltage | 陈湘宁
37 | V1.36 | 2024-04-24 | The Holding register (95) modifies the PF mode description The parameters related to PV5 are added to Input register (339-346) | 丁志鑫
38 | V1.37 | 2024-04-24 | The parameters related to PV5 are deleted from Input register (339-346) | 丁志鑫
39 | V1.38 | 2024-05-07 | 1.The total active power of PVMeter is added to Input register (339-346) 2.The variable name of PVMeter is changed from Input register (330-345) | 陈湘宁
40 | V1.39 | 2024-05-17 | 1.Dry contact on/off and SOC enable Settings are added in Holding register (237-238) | 丁志鑫
41 | V1.40 | 2024-05-23 | 1.Master and Slave DSP version and Total Version are added in Input register (341-344) | 丁志鑫
42 | V1.41 | 2024-06-07 | 1.Dry contact signal state is added in Input register 122 | 丁志鑫
43 | V1.42 | 2024-06-13 | 1.Add holding register 500~515 2、Annual and monthly electricity consumption is added in Input register 350 ~373 | 莫细红
44 | V1.43 | 2024-06-18 | 1.The AC current charging rate is added to 1A in holding register 224 | 丁志鑫
44 | V1.44 | 2024-06-18 | 1.The application mode is added in holding register 123 2、The machine model is added in holding register 516~523 | 莫细红
44 | V1.45 | 2024-06-18 | 1、The machine model (modified) is added in holding register 508~515. | 莫细红
44 | V1.46 | 2024-06-25 | 1、Change AC hybrid mode into InstallWorkMode and add new options in Holding register 76 | 莫细红
45 | V1.48 | 2024-06-26 | 1、Load control power is added in holding register 239 | 陈湘宁
46 | V1.51 | 2024-07-16 | The number range of battery in series is changed in holding register 126 | 陈湘宁
50 | V1.55 | 2024-07-26 | The upgrade Baudrate is added in holding register 66. The Baudrate setting range is changed in holding register 4. The upgrade type is changed in holding register 61. | 莫细红
51 | V1.56 | 2024-08-09 | Add input register 108 and 109 for CT1 current and CT2 current. | 丁志鑫
52 | V1.57 | 2024-08-12 | Input register 138 is added. The battery pack voltage is added in input register 138. | 丁志鑫
53 | V1.58 | 2024-08-15 | Add input register345 and add R-phase DC current in input register345 | 吴柱贤
54 | V1.59 | 2024-08-28 | Add input register 123~124 to read the chip temperature of the monitoring board and the ambient temperature | 陈成鑫
55 | V1.60 | 2024-09-05 | Change the RS485 working mode of holding register24 to BackUp mode option | 朱毅
56 | V1.61 | 2024-09-18 | Add INVMode option to holding register 73 | 朱毅
57 | V1.62 | 2024-09-18 | Change the name of INVMode to UnUsedCT in holding register73. | 陈湘宁

## protocol specification
USRT Communication Protocol
NO. | Protocol Content | Protocol function description | Details or Example | Normal Response | Abnormal Response | Comment
1 | Data Format |  | Valid slave device addresses range from 0 to 254 decimal. The addresses assigned to each slave device range from 1 to 254. 0 is the broadcast address. Each holding register and input register is a 16-bit (two-byte) unsigned integer.
2 | command format | Function code 0x3 Read holding register |  |  | 11 0x80 ¦ 0x03 ErrornumCRC (Errornum as a byte)
3 |  | Function code 0x4 Read input register |  |  | 11 0x80 ¦ 0x04 ErrornumCRC (Errornum as a byte)
4 |  | Function code 0x6 Preset single register |  |  | 11 0x80¦0x06 ErrornumCRC (Errornum as a byte)
5 |  | Function code 0x10 Preset multiple registers |  |  | 11 0x80¦0x10 ErrornumCRC (Errornum as a byte)
6 | Device information transmission mode and framework | RTU mode | When the controller is set to communicate over the Modbus network using RTU (Remote Terminal Unit) mode, each 8-bit byte in the message contains two 4-bit hexadecimal characters. Each message must be transmitted in a continuous stream.
7 |  | Format of each byte in RTU mode | Coding system: 8-bit binary, hexadecimal 0-9, A-F Each contains two hexadecimal numbers Eight-bit message field
8 |  | Per bit | An initial bit 8 data bits. The least significant bit is sent first No parity A stop bit Error check field: cyclic redundancy check（CRC）
9 |  | Baud rate of transmission | Default baud rate：9600 bps
10 |  | minimum CMD period（RS485 timeout） | 850ms Wait at least 850ms after the last CMD to send a new CMD
11 |  | Maximum data length definition | The maximum read data length is 125 characters in a read command. The maximum length of updated data in the default command is 125 characters.

## holding
Holding Register Table
register number | Variable Name | Detail | Read-write Function | Default Value | Value Range | Data Type | Unit | Memory | Comment
Group 1 |  | System Parameter
0 | OnOff | Remote On/Off | R/W | 1 | 0~1 or 0xA5 | uint16 | - | Yes | On：1 Off：0 Restart：0xA5（not save）
1 | CMD memory En | Special parameter memory enable | W | 0 | 0~1 | uint16 | - | No | It means whether these values are valid the next time you start up
2 | DeviceType | device type | R |  |  | uint16 | - | No | 1001：Single phase hybrid All-in-one RESS 1101：Three phase hybrid All-in-one RESS 1201：Single phase off-grid inverter 1301：Three phase off-grid inverter 1401：Commercial and Industrial ESS 1501：single phase on-grid inverter 1601：three phase on-grid inverter
3 | Device ID | Device communication address | R/W | 1 | 1~254 | uint16 | - | Yes | RS485 communication ID
4 | Baudrate | Select Baudrate | R/W | 0 | 0~5 | uint16 | - | Yes | 0x0000：Set the baud rate to 9600 0x0001：Set the baud rate to 38400 0x0002：Set the baud rate to 115200 0x0003：Set the baud rate to 19200 0x0004：Set the baud rate to 56000 0x0005：Set the baud rate to256000
5 | Serial NO. 15 | Serial number 15 | R/W | - | - | ASCII | - | Yes
6 | Serial NO.14 | Serial number 14 | R/W | - | - | ASCII | - | Yes
7 | Serial NO. 13 | Serial number 13 | R/W | - | - | ASCII | - | Yes
8 | Serial NO. 12 | Serial numbe 12 | R/W | - | - | ASCII | - | Yes
9 | Serial NO. 11 | Serial number 11 | R/W | - | - | ASCII | - | Yes
10 | Serial NO. 10 | Serial number 10 | R/W | - | - | ASCII | - | Yes
11 | Serial NO. 9 | Serial numbe 9 | R/W | - | - | ASCII | - | Yes
12 | Serial NO. 8 | Serial numbe 8 | R/W | - | - | ASCII | - | Yes
13 | Serial NO. 7 | Serial number 7 | R/W | - | - | ASCII | - | Yes
14 | Serial NO. 6 | Serial number 6 | R/W | - | - | ASCII | - | Yes
15 | Serial NO. 5 | Serial number 5 | R/W | - | - | ASCII | - | Yes
16 | Serial NO. 4 | Serial number 4 | R/W | - | - | ASCII | - | Yes
17 | Serial NO. 3 | Serial number 3 | R/W | - | - | ASCII | - | Yes
18 | Serial NO. 2 | Serial number 2 | R/W | - | - | ASCII | - | Yes
19 | Serial NO. 1 | Serial numbe 1 | R/W | - | - | ASCII | - | Yes
20 | Pmax H | Rated power of the inverter (High) | R | - | 0~65535 | uint16 | 0.1VA | No
21 | Pmax L | Rated power of the inverter (Low) | R | - | 0~65535 | uint16 | 0.1VA | No
22 | Pmax Bat H | Rated power of the battery (High) | R | - | 0~65535 | uint16 | 0.1W | No
23 | Pmax Bat L | Rated power of the battery (Low) | R | - | 0~65535 | uint16 | 0.1W | No
24 | BackUpMode | BackUp option | R/W | 0 | 0~1 | uint16 | 1 | Yes | 0-UPS 1-EPS
25 | Sys Year | System time-Year | R/W | 22 | 22~100 | uint16 | Year | No | 2000+Sys Year
26 | Sys Month | System time-Month | R/W | 1 | 1~12 | uint16 | Month | No
27 | Sys Day | System time-Day | R/W | 1 | 1~31 | uint16 | Day | No
28 | Sys Hour | System time-Hour | R/W | 0 | 0~59 | uint16 | Hour | No
29 | Sys Min | System time-Minute | R/W | 0 | 0~59 | uint16 | Minute | No
30 | Sys Sec | System time-Second | R/W | 0 | 0~59 | uint16 | Second | No
31 | Sys Weekly | System week | R/W | 1 | 1~7 | uint16 | - | No
32 | SaftyFuncEn | System security function enable bit | R/W | - | 0~65535 | uint16 | - | Yes
33 | Fw version H | firmware version (High) | R | - |  | ASCII | - | No | Certified version（XX1.0）
34 | Fw version M | firmware version (Medium) | R | - |  | ASCII | - | No
35 | Fw version L | firmware version (Low) | R | - |  | ASCII | - | No
36 | M3 version Name H | Communication firmware version name | R | - |  | ASCII | - | No | M3 software version（XXXX0000）
37 | M3 version Name L | Communication firmware version name | R | - |  | ASCII | - | No
38 | M3 version No | Communication firmware version number | R | - |  | uint16 | - | No
39 | Hard version | hardware version | R | - |  | uint16 | - | No | hardware version
40 | Manufacturer Info 8 | Manufacturer information 8 | R | - |  | ASCII | - | No | Manufacturer information
41 | Manufacturer Info 7 | Manufacturer information 7 | R | - |  | ASCII | - | No
42 | Manufacturer Info 6 | Manufacturer information 6 | R | - |  | ASCII | - | No
43 | Manufacturer Info 5 | Manufacturer information 5 | R | - |  | ASCII | - | No
44 | Manufacturer Info 4 | Manufacturer information 4 | R | - |  | ASCII | - | No
45 | Manufacturer Info3 | Manufacturer information 3 | R | - |  | ASCII | - | No
46 | Manufacturer Info 2 | Manufacturer information 2 | R | - |  | ASCII | - | No
47 | Manufacturer Info 1 | Manufacturer information 1 | R/W | - | 0~4 | ASCII/uint16 | - | Yes | The manufacturer name can be selected when configured
48 | FW Build No. 5 | Model version number（TJ） | R | - |  | ASCII | - | No | System software version（XXXX000000）
49 | FW Build No. 4 | Model version number（AA） | R | - |  | ASCII | - | No
50 | FW Build No. 3 | DSP1 Software digital version number | R | - |  | ASCII | - | No
51 | FW Build No. 2 | DSP2 Software digital version number | R | - |  | ASCII | - | No
52 | FW Build No. 1 | M3 Software digital version number | R | - |  | ASCII | - | No
53 | FW Build No. 0 | Other firmware Software digital version number | R | - |  | ASCII | - | No
54 | ModbusVersion | Modbus Version | R | - | - | uint16 | - | No | Communication protocol version(01)
55 | Module 4 | Inverter mode(4) | R/W | - | - | uint16 | - | Yes
56 | Module 3 | Inverter mode(3) | R/W | - | - | uint16 | - | Yes
57 | Module 2 | Inverter mode(2) | R/W | - | - | uint16 | - | Yes
58 | Module 1 | Inverter mode(1) | R/W | - | - | uint16 | - | Yes
59 | Reset to factory | restore factory setting | W | - | - | uint16 | - | No | 0xA0：restore factory setting 0x01：restore user data
60 | UpdateDeviceID | ID of the currently updating device | R | - | - | uint16 | - | No | H:Device type L： Device ID
61 | UpdateState | Updating progress of the firmware | R/W | - | - | uint16 | - | No | read（0~100：updating process over 100：update fault code.The transfer progress of 0% is also an upgrade fault.） settings（0x01：bin upgrade；0x10：Hex upgrade ，0x11：upg upgrade）
62 | CountrySelected（reserved） | select region and country or not | R/W | - | - | uint16 | - | Yes | 0: need to select; 1: selected
63 | Active P Rate | The maximum output active power percentage of the inverter | R/W | 100 | 0~100 | uint16 | 0.01 | Yes
64 | Reactive P Rate | Maximum output reactive power percentage of the inverter | R/W | 100 | 0~100 | uint16 | 0.01 | Yes
65 | Power factor | Inverter output power factor | R/W | 10000 | 0~20000 | uint16 |  | Yes
66 | Update_Baudrate | Updating Baudrate | R/W | 0 |  | uint16 |  | Yes | 0x0000：Set the baud rate to 9600； 0x0001：Set the baud rate to 38400； 0x0002：Set the baud rate to 115200 0x0003：Set the baud rate to 19200； 0x0004：Set the baud rate to 56000； 0x0005：Set the baud rate to 256000
67 | TrakerModel | MPPT mode | R/W |  |  | uint16 |  | Yes | 0:independent MPPT mode 1:DC source mode 2:multiple MPPT mode
68 | PV Power Limit Rate | Maximum PV output power percentage | R/W | 100 | 0~100 | uint16 | 1 | Yes
69 | Vpv start | Input starting voltage | R/W |  |  | uint16 | 0.1V | Yes
70 | PV Voltage Low Fault | Turn-off voltage | R/W |  |  | uint16 | 0.1V | Yes
71 | PowerCtrMode | Remote power regulation mode | R/W | 0 | 0~1 | uint16 |  | 否 | 0:normal mode 1:slope mode
72 | PowerCtrRate | Remote power regulation rate | R/W | 33 |  | uint16 | 0.1%Pn/min | Yes | German security requirements
73 | CTMode | METER/CT mode selection | R/W |  |  | uint16 |  | Yes | 0：METER 1：CT 2：UnUsedCT
74 | LocalAntiBackflowEnable | Anti-reverse current Enable | R/W | 0 | 0~3 | uint16 |  | Yes | 0：Disable 1：Anti-reverse current enable 3：three phase independent anti-reverse current function enable
75 | BackflowMeterPowerLimit | power limit value of anti-reverse current | R/W | 0 |  | uint16 | 0.1% | Yes
76 | BackflowHostNoResponseFlag | anti-reverse failure flag bit | R | 0 |  | uint16 |  | Yes | 0:normal 1：fail
77 | BackflowFaultTime | Failure time for anti-reverse current | R/W | 30 | 0~65535 | uint16 | 1s | Yes
78 | BackflowFaultPowerRate | active power percentage of anti-reverse current failure | R/W | 50 | 0~100 | uint16 | 0.1% | Yes | The machine will work according to the given power after anti-reverse current failure
79 | InstallWorkModeSet | AC Couple inverter setting | R/W | 0 |  | uint16 | 1 | Yes | 0:DC Couple 1：AC Couple 2：Hybrid
80 | LocalAntiBackflow Hard Enable | Anti-reverse current hardware Enable | R/W | 0 | 0~1 | uint16 | 1 | Yes | 0：Disable 1：Enable
81 | N-PE Enable | N-PE Enable | R/W | 0 | 0~1 | uint16 | 1 | Yes | 0：Disable 1：Enable
82 | batDealSet | Battery match protocol settings | R/W | 0 | 0~15 | uint16 |  | Yes | 0：PYLON 1：HINEN 2：Growatt 3：Growcol 4：SHOTO 5：GoodWE 6：YUZEI
83 | Vac low C | The lowest voltage connected to the grid | R/W |  | <Vn | uint16 | 0.1V | Yes
84 | Vac high C | The highest voltage connected to the grid | R/W |  | >Vn | uint16 | 0.1V | Yes
85 | Fac low C | The lowest frequency connected to the grid | R/W |  | <Fn | uint16 | 0.01Hz | Yes
86 | Fac high C | The highest frequency connected to the grid | R/W |  | >Fn | uint16 | 0.01Hz | Yes
87 | reserve | reserve |  |  |  | uint16
88 | NominalEPSVolt | selectable rated off-grid voltage | R/W | 0 | 0~4 | uint16 | 0.1V | Yes | 0:230V 1:240V 2:220V 3:208V 4:200
89 | NominalEPSFre | selectable rated off-grid frequency | R/W | 0 | 0~1 | uint16 | 0.01Hz | Yes | 0:50Hz 1:60Hz
90 | EPS En | Off-grid function enable | R/W | 1 | 0~1 | uint16 |  | Yes
91 | Bypass En | Bypass mode enable | R/W | 0 | 0~1 | uint16 |  | Yes
92 | UPS En | UPSfunction enable | R/W | 0 | 0~1 | uint16 |  | Yes
93 | H_LVRT Enable | High-low voltage ride-through enable | R/W | 0 | 0~1 | uint16 | 1 | Yes | 0：Disable 1：Enable
94 | bSafetyId | Safety ID number | R/W | 0 | 0~255 | uint16 |  | Yes
95 | PFModel | PF function mode setting | R/W | 0 | 0~9 | uint16 |  | Yes | 0: PF=1 1: PF value setting 2: Default PF curve 3:User-defined PF curve mode 4: lagging reactive power（+） 5: leading reactive power（-） 6：Q(v) mode 7：Positive and negative reactive power value adjustment 8: Static capacitive QV mode 9: Static inductive QV mode
96 | V1S | CEI021 V1S Q(v) | R/W |  | >Vn | uint16 | 0.1V | Yes
97 | V2S | CEI021 V2S Q(v) | R/W |  | >Vn | uint16 | 0.1V | Yes
98 | V1L | CEI021 V1L Q(v) | R/W |  | <Vn | uint16 | 0.1V | Yes
99 | V2L | CEI021 V2L Q(v) | R/W |  | <Vn | uint16 | 0.1V | Yes
100 | QpercentMax | Qmax of Q（V） curve | R/W |  |  | uint16 | 0.001 | Yes
101 | Qlockinpower | Q(v) lock in active power | R/W |  |  | uint16 | 0.1% | Yes
102 | QlockOutpower | Q(v) lock out active power | R/W |  |  | uint16 | 0.1% | Yes
103 | QVRPDelayTime | QV reactive power delay time | R/W |  |  | uint16 | 20ms | Yes
104 | PFLockInGridV | Lock in PF line voltage | R/W |  |  | uint16 | 0.1V | Yes
105 | PFLockOutGridV | Lock out PF line voltage | R/W |  |  | uint16 | 0.1V | Yes
106 | QVPowerStableTime | QV reactive power stablization time | R/W |  |  | uint16 | 20ms | Yes
107 | reserve | reserve
108 | u8OFFGridConstantPowerEn | off-grid constant power enable | R/W | 0 |  | uint16 | 1 | Yes
109 | QVKrate | reserve
110 | QpercentMin | Qmin of Q（V）curve | R/W |  |  | uint16 | 0.001 | Yes
111 | IsLandEn | Anti-islanding enable | R/W | 0 | 0~1 | uint16 |  | Yes | 0：Disable 1：Enable
112 | DRMS EN | logic interface enable | R/W | 0 | 0~1 | uint16 |  | Yes | 0：Disable 1：Enable
113 | ZeroCurrentEnable | zero current mode enable | R/W | 0 | 0~1 | uint16 |  | Yes | 0：Disable 1：Enable
114 | ZeroCurrentStaticlowVolt | zero current static low voltage | R/W |  | <Vn | uint16 | 0.1V | Yes
115 | ZeroCurrentStaticHighVolt | zero current static high voltage | R/W |  | >Vn | uint16 | 0.1V | Yes
116 | ZeroCurrentStaticlowFreq | zero current static low frequency | R/W |  | <Fn | uint16 | 0.01Hz | Yes
117 | ZeroCurrentStaticHighFreq | zero current static high frequency | R/W |  | >Fn | uint16 | 0.01Hz | Yes
118 | AustraliaRegion | safety regulation selection for Australia region | R/W |  |  | uint16 |  |  | 0：REGION_A 1：REGION_B 2：REGION_C 3：REGION_NZ
119 | AcOutMode | Inverter AC output parallel mode | R/W | 0 | 0-4 | uint16 | 1 | Yes
120 | QP_p1 Rate | Active power percentage start point of the default PF curve | R/W | 50 | 0-100 | uint16 | 0.01 | Yes
121 | Q2percent | reactive power Q2 at under voltage starting point of Q（V）curve | R/W | 0 | 0-1000 | uint16 | 0.001 | Yes
122 | Q3percent | reactive power Q3 at over voltage starting point of Q（V）curve | R/W | 0 | 0-1000 | uint16 | 0.001 | Yes
123 | Application_Mode | application mode | R/W | 0 | 0-10 | uint16 | 1 | Yes | 0：NULL 1：Charging_Station_Mode（与ACCouple排斥）
Group 2 |  | Battery Parameter
125 | BatteryType | Battery Type | R/W | 1 |  |  |  |  | 0：Lead-acid battery 1：Lithium battery 2：Others
126 | BatMdlSerialNum | Number of batteries in series; | R/W | 1 | 1~66 | uint16 |  | Yes | Lead-acid battery
127 | BatMdlParallNum | Number of parallel batteries; | R/W | 1 | 1~160 | uint16 |  | Yes | Lead-acid battery
128 | Float charge current limit | CC current | R/W | 850 |  | uint16 | 0.01A | Yes | When the charging current needs to be lower than this value, enter the floating charge CC.
129 | VbatStopForDischarge | LV voltage | R/W | 460 |  | uint16 | 0.01V | Yes
130 | Vbat constant charge | CV voltage | R/W | 580 |  | uint16 | 0.01V | Yes | CV voltage（Lead-acid battery）
131 | Battemp lower limit d | The Lowest temperature limit of lead-acid battery discharge | R/W |  |  | uint16 | 0.1C° | Yes
132 | Bat temp upper limit d | The highest temperature limit of lead-acid battery discharge | R/W |  |  | uint16 | 0.1C° | Yes
133 | Bat temp lower limit c | The Lowest temperature limit of lead-acid battery charge | R/W |  |  | uint16 | 0.1C° | Yes
134 | Bat temp upper limit c | The highest temperature limit of lead-acid battery charge | R/W |  |  | uint16 | 0.1C° | Yes
135 | OfflineDischargeStopSOC | cutoff SOC of Off-grid discharge | R/W | 20 |  | uint16 | 1% | Yes
136 | loadFirstChargeRate | charge power in load priority | R/W | 100 |  | uint16 | 0.01 | Yes
137 | loadFirstChargeRate | discharge power in load priority | R/W | 100 |  | uint16 | 0.01 | Yes
138 | BatFirst stop SOC | cutoff SOC of charge | R/W | 100 |  | uint16 | 0.01 | Yes
139 | GridFirstStop SOC | cutoff SOC of discharge | R/W | 5 |  | uint16 | 0.01 | Yes
140 | LoadFirstStopSoc | Scutoff SOC of discharge in load priority | R/W | 10 |  | uint16 | 0.01 | Yes
141 | RemotePowerControlEn | quick setting control enable for charge and discharge | R/W | 0 |  | uint16 |  | Yes
142 | RemotePowerControlTime | quick setting for charge and discharge duration | R/W | 0 |  | uint16 | 1s | Yes
143 | RemotePowerControlRate | quick setting for charge and discharge power | R/W | 0 | 100~-100 | uint16 | 0.01 | Yes | positive：charge negative：discharge
144 | AC charge En | AC charge enable | R/W | 0 | 0~1 | uint16 |  | Yes | 0：Disable 1：Enable
145 | LoadFirstDischargeDisableFlag | discharge disable flag in load priority | R/W | 0 | 0~1 | uint16 |  | Yes | 0：unban 1：ban
146 | reserve | reserve | [5 empty] | Yes
147 | NumberTimePeriods | Number of charging and discharging time periods | R/W | 0 | 0~20 | uint16 |  | Yes | If the value is set to 0xA5, all time periods are initialized to 0. Time period power is 0.
148 | PeriodTimeStart1 | Time period 1 Starting time | R/W | 0 | 0~1440 | uint16 | 1min | Yes | Set time = hour x 60+ minutes The end time is longer than the start time
149 | PeriodTimeEnd1 | Time period 1 ending time | R/W | 0 | 0~1440 | uint16 | 1min | Yes
150 | PeriodTimeRate1 | Time period 1 charge and discharge power | R/W | 0 | 100~-100 | uint16 | 1Pn% | Yes | positive：charge negative：discharge
151 | PeriodTimeStart2 | Time period 2 Starting time | R/W | 0 | 0~1440 | uint16 | 1min | Yes | Set time = hour x 60+ minutes The end time is longer than the start time.
152 | PeriodTimeEnd2 | Time period 2 ending time | R/W | 0 | 0~1440 | uint16 | 1min | Yes
153 | PeriodTimeRate2 | Time period 2 charge and discharge power | R/W | 0 | 100~-100 | uint16 | 1Pn% | Yes | positive：charge negative：discharge
154 | PeriodTimeStart3 | Time period 3 Starting time | R/W | 0 | 0~1440 | uint16 | 1min | Yes | Set time = hour x 60+ minutes The end time is longer than the start time.
155 | PeriodTimeEnd3 | Time period 3 ending time | R/W | 0 | 0~1440 | uint16 | 1min | Yes
156 | PeriodTimeRate3 | Time period 3 charge and discharge power | R/W | 0 | 100~-100 | uint16 | 1Pn% | Yes | positive：charge negative：discharge
157 | PeriodTimeStart4 | Time period 4 Starting time | R/W | 0 | 0~1440 | uint16 | 1min | Yes | Set time = hour x 60+ minutes The end time is longer than the start time.
158 | PeriodTimeEnd4 | Time period 4 ending time | R/W | 0 | 0~1440 | uint16 | 1min | Yes
159 | PeriodTimeRate4 | Time period 4 charge and discharge power | R/W | 0 | 100~-100 | uint16 | 1Pn% | Yes | positive：charge negative：discharge
160 | PeriodTimeStart5 | Time period 5 Starting time | R/W | 0 | 0~1440 | uint16 | 1min | Yes | Set time = hour x 60+ minutes The end time is longer than the start time.
161 | PeriodTimeEnd5 | Time period 5 ending time | R/W | 0 | 0~1440 | uint16 | 1min | Yes
162 | PeriodTimeRate5 | Time period 5 charge and discharge power | R/W | 0 | 100~-100 | uint16 | 1Pn% | Yes | positive：charge negative：discharge
163 | PeriodTimeStart6 | Time period 6 Starting time | R/W | 0 | 0~1440 | uint16 | 1min | Yes | Set time = hour x 60+ minutes The end time is longer than the start time.
164 | PeriodTimeEnd1 | Time period 6 ending time | R/W | 0 | 0~1440 | uint16 | 1min | Yes
165 | PeriodTimeRate1 | Time period 6 charge and discharge power | R/W | 0 | 100~-100 | uint16 | 1Pn% | Yes | positive：charge negative：discharge
166 | PeriodTimeStart7 | Time period 7 Starting time | R/W | 0 | 0~1440 | uint16 | 1min | Yes | Set time = hour x 60+ minutes The end time is longer than the start time.
167 | PeriodTimeEnd1 | Time period 7 ending time | R/W | 0 | 0~1440 | uint16 | 1min | Yes
168 | PeriodTimeRate1 | Time period 7 charge and discharge power | R/W | 0 | 100~-100 | uint16 | 1Pn% | Yes | positive：charge negative：discharge
169 | PeriodTimeStart8 | Time period 8 Starting time | R/W | 0 | 0~1440 | uint16 | 1min | Yes | Set time = hour x 60+ minutes The end time is longer than the start time.
170 | PeriodTimeEnd1 | Time period 8 ending time | R/W | 0 | 0~1440 | uint16 | 1min | Yes
171 | PeriodTimeRate1 | Time period 8 charge and discharge power | R/W | 0 | 100~-100 | uint16 | 1Pn% | Yes | positive：charge negative：discharge
172 | PeriodTimeStart9 | Time period 9 Starting time | R/W | 0 | 0~1440 | uint16 | 1min | Yes | Set time = hour x 60+ minutes The end time is longer than the start time.
173 | PeriodTimeEnd1 | Time period 9 ending time | R/W | 0 | 0~1440 | uint16 | 1min | Yes
174 | PeriodTimeRate1 | Time period 9 charge and discharge power | R/W | 0 | 100~-100 | uint16 | 1Pn% | Yes | positive：charge negative：discharge
175 | PeriodTimeStart10 | Time period 10 Starting time | R/W | 0 | 0~1440 | uint16 | 1min | Yes | Set time = hour x 60+ minutes The end time is longer than the start time.
176 | PeriodTimeEnd10 | Time period 10 ending time | R/W | 0 | 0~1440 | uint16 | 1min | Yes
177 | PeriodTimeRate10 | Time period 10 charge and discharge power | R/W | 0 | 100~-100 | uint16 | 1Pn% | Yes | positive：charge negative：discharge
178 | PeriodTimeStart11 | Time period 11 Starting time | R/W | 0 | 0~1440 | uint16 | 1min | Yes | Set time = hour x 60+ minutes The end time is longer than the start time.
179 | PeriodTimeEnd11 | Time period 11 ending time | R/W | 0 | 0~1440 | uint16 | 1min | Yes
180 | PeriodTimeRate11 | Time period 11 charge and discharge power | R/W | 0 | 100~-100 | uint16 | 1Pn% | Yes | positive：charge negative：discharge
181 | PeriodTimeStart12 | Time period 12 Starting time | R/W | 0 | 0~1440 | uint16 | 1min | Yes | Set time = hour x 60+ minutes The end time is longer than the start time.
182 | PeriodTimeEnd12 | Time period 12 ending time | R/W | 0 | 0~1440 | uint16 | 1min | Yes
183 | PeriodTimeRate12 | Time period 12 charge and discharge power | R/W | 0 | 100~-100 | uint16 | 1Pn% | Yes | positive：charge negative：discharge
184 | PeriodTimeStart13 | Time period 13 Starting time | R/W | 0 | 0~1440 | uint16 | 1min | Yes | Set time = hour x 60+ minutes The end time is longer than the start time.
185 | PeriodTimeEnd13 | Time period 13 ending time | R/W | 0 | 0~1440 | uint16 | 1min | Yes
186 | PeriodTimeRate13 | Time period 13 charge and discharge power | R/W | 0 | 100~-100 | uint16 | 1Pn% | Yes | positive：charge negative：discharge
187 | PeriodTimeStart14 | Time period 14 Starting time | R/W | 0 | 0~1440 | uint16 | 1min | Yes | Set time = hour x 60+ minutes The end time is longer than the start time.
188 | PeriodTimeEnd14 | Time period 14 ending time | R/W | 0 | 0~1440 | uint16 | 1min | Yes
189 | PeriodTimeRate14 | Time period 14 charge and discharge power | R/W | 0 | 100~-100 | uint16 | 1Pn% | Yes | positive：charge negative：discharge
190 | PeriodTimeStart15 | Time period 15 Starting time | R/W | 0 | 0~1440 | uint16 | 1min | Yes | Set time = hour x 60+ minutes The end time is longer than the start time.
191 | PeriodTimeEnd15 | Time period 15 ending time | R/W | 0 | 0~1440 | uint16 | 1min | Yes
192 | PeriodTimeRate15 | Time period 15 charge and discharge power | R/W | 0 | 100~-100 | uint16 | 1Pn% | Yes | positive：charge negative：discharge
193 | PeriodTimeStart16 | Time period 16 Starting time | R/W | 0 | 0~1440 | uint16 | 1min | Yes | Set time = hour x 60+ minutes The end time is longer than the start time.
194 | PeriodTimeEnd16 | Time period 16 ending time | R/W | 0 | 0~1440 | uint16 | 1min | Yes
195 | PeriodTimeRate16 | Time period 16 charge and discharge power | R/W | 0 | 100~-100 | uint16 | 1Pn% | Yes | positive：charge negative：discharge
196 | PeriodTimeStart17 | Time period 17 Starting time | R/W | 0 | 0~1440 | uint16 | 1min | Yes | Set time = hour x 60+ minutes The end time is longer than the start time.
197 | PeriodTimeEnd17 | Time period 17 ending time | R/W | 0 | 0~1440 | uint16 | 1min | Yes
198 | PeriodTimeRate17 | Time period 17 charge and discharge power | R/W | 0 | 100~-100 | uint16 | 1Pn% | Yes | positive：charge negative：discharge
199 | PeriodTimeStart18 | Time period 18 Starting time | R/W | 0 | 0~1440 | uint16 | 1min | Yes | Set time = hour x 60+ minutes The end time is longer than the start time.
200 | PeriodTimeEnd18 | Time period 18 ending time | R/W | 0 | 0~1440 | uint16 | 1min | Yes
201 | PeriodTimeRate18 | Time period 18 charge and discharge power | R/W | 0 | 100~-100 | uint16 | 1Pn% | Yes | positive：charge negative：discharge
202 | PeriodTimeStart19 | Time period 19 Starting time | R/W | 0 | 0~1440 | uint16 | 1min | Yes | Set time = hour x 60+ minutes The end time is longer than the start time.
203 | PeriodTimeEnd19 | Time period 19 ending time | R/W | 0 | 0~1440 | uint16 | 1min | Yes
204 | PeriodTimeRate19 | Time period 19 charge and discharge power | R/W | 0 | 100~-100 | uint16 | 1Pn% | Yes | positive：charge negative：discharge
205 | PeriodTimeStart20 | Time period 20 Starting time | R/W | 0 | 0~1440 | uint16 | 1min | Yes | Set time = hour x 60+ minutes The end time is longer than the start time.
206 | PeriodTimeEnd20 | Time period 20 ending time | R/W | 0 | 0~1440 | uint16 | 1min | Yes
207 | PeriodTimeRate20 | Time period 20 charge and discharge power | R/W | 0 | 100~-100 | uint16 | 1Pn% | Yes | positive：charge negative：discharge
208 | ChargePowerPercent | actual charging percentage at present | R | 0 | 100~0 | uint16 | 1Pn% | Yes
209 | DischargePowerPercent | actual discharging percentage at present | R | 0 | 100~0 | uint16 | 1Pn% | Yes
210 | DspBeepOnOff | Alarm buzzer on/off | R/W | 1 | 0~1 | uint16 |  | Yes | Off-grid inverter parameters
211 | M3BeepOnOff | button buzzer on/off | R/W | 1 | 0~1 | uint16 |  | Yes | Off-grid inverter parameters
212 | OverloadToBypass | If the inverter is 1.5 times overloaded, change to bypass or not | R/W | 1 | 0~1 | uint16 |  | Yes | Off-grid inverter parameters
213 | BatUnderVol | shutdown point of low voltage inverter with battery | R/W | 40V | 40.0~55.0 | uint16 | 0.1V | Yes | Off-grid inverter parameters
214 | SourcePriority | energy supply priority | R/W | 0 |  | uint16 |  | Yes | SOL UTI SUB
215 | Equalization | Equalization function enable on/off | R/W | 0 | 0~1 | uint16 |  | Yes | Off-grid inverter parameters
216 | EQBatteryVoltage | Equalization charging volatge point setting | R/W | 58.4 | 48.0~61.0 | uint16 | 0.1V | Yes | Off-grid inverter parameters
217 | EQBatteryTime | Equalization charging duration | R/W | 60 | 5~900 | uint16 | min | Yes | Off-grid inverter parameters
218 | EQBatteryTimeout | Equalization Charge timeout exit | R/W | 120 | 5~900 | uint16 | min | Yes | Off-grid inverter parameters
219 | EqualizationCycle | Equalization cycle period | R/W | 30 | 1~90 | uint16 |  | Yes | Off-grid inverter parameters
220 | EqualizationImmediately | Execute Equalization enable on/off immediately | R/W | 0 | 0~1 | uint16 |  | Yes | Off-grid inverter parameters
221 | Grid_tieOperation | Grid-tied enegry feed function on/off | R/W | 0 | 0~1 | uint16 |  | Yes | Off-grid inverter parameters
222 | uwFloatV_Lead | floating charge voltage | R/W |  |  |  | 0.01V
223 | AcInputType | AC input device | R/W | [5 empty] | APL UPS GEN
224 | AcChargingCurrent | AC Charge limiting current | R/W |  |  |  | 1A
225 | ChargeSourcePriority | Charging device priority | R/W
226 | stEQEnableTime.bYears | Equalization time setting or the last time it started | R
227 | stEQEnableTime.bMonths |  | R
228 | stEQEnableTime.bDays |  | R
229 | stEQEnableTime.bHours |  | R
230 | stEQEnableTime.bMinutes |  | R
231 | stEQEnableTime.bSeconds |  | R
232 | EQRunFlag | Equalization Actual operating state | R |  |  | uint16
233 | SetSocForHeatPump1 | set SOC enable point for device 1 such as heat pump | R/W | 95 | 0-100 | uint16 | 1 | Yes
234 | SetSocForHeatPump2 | set SOC enable point for device 2 such as heat pump | R/W | 95 |  | uint16 |  | Yes
235 | SetSocForHeatPump3 | set SOC enable point for device 3 such as heat pump | R/W | 95 |  | uint16 |  | Yes
236 | SetHeatPumOnOffWay | The user sets the on/off mode of the device, such as the heat pump | R/W | 0 |  |  |  | Yes | （1-ON，0-OFF,2-SOC） bit00-bit03: Heat pump device 1 ON/OFF bit04-bit07:Heat pump device 2 ON/OFF bit08-bit11:Heat pump device 3 ON/OFF bit12-bit15:Reserve
237 | DryContactSwitch | dry contact on/off enable | R/W | 0 | 0-2 | uint16 |  |  | 0:Disconnect the dry contact relay 1:Dry contact relay is off. 2:The dry contact relay is automatically controlled by register 238.
238 | DryContactStartSOC | dry contact start SOC | R/W | 20 | 0-100 | uint16 |  |  | 237项选择2时有效
239 | u16LoadCtrlPower | Load control power | R/W | 36000 |  | uint32 | W | Yes
240 | u8ParallelID | Parallel ID Settings | R/W |  | 2024-01-06 | uint16 |  | Yes
240~248 | reserve | reserve
249 | reserve | reserve
Group 3 |  | Safety parameter
250 | Vac low1 | First order protection of low grid voltage | R/W |  | <Vn | uint16 | 0.1V | Yes
251 | Vac high1 | First order protection of high grid voltage | R/W |  | >Vn | uint16 | 0.1V | Yes
252 | Fac low1 | First order protection of low grid frequency | R/W |  | <Fn | uint16 | 0.01Hz | Yes
253 | Fac high1 | First order protection of high grid frequency | R/W |  | >Fn | uint16 | 0.01Hz | Yes
254 | Vac low 2 | Second order protection of low grid voltage | R/W |  | <Vn | uint16 | 0.1V | Yes
255 | Vac high 2 | Second order protection of high grid voltage | R/W |  | >Vn | uint16 | 0.1V | Yes
256 | Fac low 2 | Second order protection of low grid frequency | R/W |  | <Fn | uint16 | 0.01Hz | Yes
257 | Fac high 2 | Second order protection of high grid frequency | R/W |  | >Fn | uint16 | 0.01Hz | Yes
258 | Vac low 3 | Third order protection of low grid voltage | R/W |  | <Vn | uint16 | 0.1V | Yes
259 | Vac high 3 | Third order protection of high grid voltage | R/W |  | >Vn | uint16 | 0.1V | Yes
260 | Fac low 3 | Third order protection of low grid frequency | R/W |  | <Fn | uint16 | 0.01Hz | Yes
261 | Fac high 3 | Third order protection of high grid frequency | R/W |  | >Fn | uint16 | 0.01Hz | Yes
262 | Vac low1 time | First order protection time of low grid voltage | R/W |  | 0~5000 | uint16 | 20ms | Yes
263 | Vac high1 time | First order protection time of high grid voltage | R/W |  | 0~5000 | uint16 | 20ms | Yes
264 | Fac low1 time | First order protection time of low grid frequency | R/W |  | 0~5000 | uint16 | 20ms | Yes
265 | Fac high1 time | First order protection time of high grid frequency | R/W |  | 0~5000 | uint16 | 20ms | Yes
266 | Vac low2 time | Second order protection time of low grid voltage | R/W |  | 0~5000 | uint16 | 20ms | Yes
267 | Vac high2 time | Second order protection time of high grid voltage | R/W |  | 0~5000 | uint16 | 20ms | Yes
268 | Fac low2 time | Second order protection time of low grid frequency | R/W |  | 0~5000 | uint16 | 20ms | Yes
269 | Fac high2 time | Second order protection time of high grid frequency | R/W |  | 0~5000 | uint16 | 20ms | Yes
270 | Vac low3 time | Third order protection time of low grid voltage | R/W |  | 0~5000 | uint16 | 20ms | Yes
271 | Vac high3 time | Third order protection time of high grid voltage | R/W |  | 0~5000 | uint16 | 20ms | Yes
272 | Fac low3 time | Third order protection time of low grid frequency | R/W |  | 0~5000 | uint16 | 20ms | Yes
273 | Fac high3 time | Third order protection time of high grid frequency | R/W |  | 0~5000 | uint16 | 20ms | Yes
274 | U10min | Voltage protection for ten minutes | R/W |  |  | uint16 | 0.1V | Yes
275 | U10minTime | average voltage protection time in ten minutes | R/W |  |  | uint16 | 20ms | Yes
276 | Time start | grid-tied time | R/W |  | >30 | uint16 | 1s | Yes
277 | RestartDelayTime | grid-reconnected time | R/W |  | >30 | uint16 | 1s | Yes
278 | PowerStartSlope | loading rate | R/W |  | 1-30000 | uint16 | 0.1Pn%/min | Yes
279 | PowerRestartSlopeEE | Restart loading rate | R/W |  | 1-30000 | uint16 | 0.1Pn%/min | Yes
280 | reserve | [7 empty] | Reserved. This was previously repeated with register 72, so deleted.
281 | vol-watt en | voltage active power enable | R/W | 0 | 0~1 | uint16 |  | Yes
282 | VWH_End | End point of derating of high grid voltage | R/W |  | >Vn | uint16 | 0.1V | Yes
283 | VWH_Start | Start point of derating of high grid voltage | R/W |  | >Vn | uint16 | 0.1V | Yes
284 | VWL_End | End point of low grid voltage upload | R/W |  | <Vn | uint16 | 0.1V | Yes
285 | VWL_Start | Start point at low grid voltage upload | R/W |  | <Vn | uint16 | 0.1V | Yes
286 | OVWattStopPower | power at end point of overvoltage derating | R/W |  |  | uint16 | 1% | Yes
287 | GridWattDelay | The delay time of voltage active power | R/W |  |  | uint16 | 20ms | Yes
288 | UVWattStopPower | power at end point of undervoltage derating | R/W |  |  | uint16 | 1% | Yes
289 | VwattResponseTime | Voltage active power stabilization time | R/W |  |  | uint16 | 20ms | Yes
290 | UVWattStartPower | power at starting point of undervoltage derating | R/W | 20 | 0-100 | uint16 | 1% | Yes | PU_P2
291 | OVWattStartPower | power at start point of overvoltage derating | R/W | 20 | 0-100 | uint16 | 1% | Yes | PU_P3
292 | reserve | reserve
293 | reserve | reserve
294 | OFDeratCurveEn | Overfrequency derating enable | R/W | 0 | 0~1 | uint16 |  | Yes
295 | OFreqPoint | Frequency derating point | R/W |  |  | uint16 | 0.01Hz | Yes
296 | OFreqEndPoint | over frequency end point | R/W |  |  | uint16 | 0.01Hz | Yes
297 | OFDeratRate | over frequency derate rate | R/W |  |  | uint16 | 0.001 | Yes
298 | OverFDeratResponseTime | over frequency derate response time | R/W |  |  | uint16 | 20ms | Yes
299 | OFDerateRecoverPoint | over frequency derate recover point | R/W |  |  | uint16 | 0.01Hz | Yes
300 | OFDerateRecoverDelayTime | over frequency derate recover delay time | R/W |  |  | uint16 | 20ms | Yes
301 | FreqDerateZeroPowerPoint | frequency derate zero power point | R/W |  |  | uint16 | 0.01Hz | Yes
302 | OFDeratDelayTime | over frequency derate delay time | R/W |  |  | uint16 | 20ms | Yes
303 | reserve | reserve
304 | reserve | reserve
305 | reserve | reserve
306 | LFUploadEN | under frequency upload Enable | R/W | 0 | 0~1 | uint16 |  | Yes
307 | UFreqPoint | under frequency upload point | R/W |  |  | uint16 | 0.01Hz | Yes
308 | UFreqEndPoint | end point of under frequency upload | R/W |  |  | uint16 | 0.01Hz | Yes
309 | UFUploadDelayTime | under frequency upload delay time | R/W |  |  | uint16 | 20ms | Yes
310 | UFUploadRate | under frequency upload rate | R/W |  |  | uint16 | 0.001 | Yes
311 | UFUploadResponseTime | under frequency upload response time | R/W |  |  | uint16 | 20ms | Yes
312 | UFRebackPoint | under frequency upload recover point | R/W |  |  | uint16 | 0.001 | Yes
313 | UFUploadRecoverTime | under frequency upload recover delay time | R/W |  |  | uint16 | 20ms | Yes
314 | UFZeroPowerPoint | under frequency zero power point | R/W |  |  | uint16 | 0.01Hz | Yes
315 | GridRestart_H_Freq | grid restart high frequency point | R/W |  |  | uint16 | 0.01Hz | Yes
316 | LocalSafetyCmd | user safety selection command | R/W | 0 |  | uint16 |  | Yes | 0：Local standard safety regulations 1：User wide range 2：Power grid company safety regulations
317 | reserve | reserve
318 | reserve | reserve
319 | reserve | reserve
320 | reserve | reserve
321 | reserve | reserve
322 | reserve | reserve
323 | SpecPasswordType | Unlock or set a security password | W |  |  | uint16 |  | No
324 | SpecPassword3 | Specification Password 3 | W |  |  | uint16 |  | No
325 | SpecPassword2 | Specification Password 2 | W |  |  | uint16 |  | No
326 | SpecPassword1 | Specification Password 1 | W |  |  | uint16 |  | No
327 | PeriodTime1StopSOC | Period 1 cutoff SOC | R/W |  |  | uint16 | %
328 | PeriodTime2StopSOC | Period 2 cutoff SOC | R/W |  |  | uint16 | %
329 | PeriodTime3StopSOC | Period 3 cutoff SOC | R/W |  |  | uint16 | %
330 | PeriodTime4StopSOC | Period 4 cutoff SOC | R/W |  |  | uint16 | %
331 | PeriodTime5StopSOC | Period 5 cutoff SOC | R/W |  |  | uint16 | %
332 | PeriodTime6StopSOC | Period 6 cutoff SOC | R/W |  |  | uint16 | %
333 | PeriodTime7StopSOC | Period 7 cutoff SOC | R/W |  |  | uint16 | %
334 | PeriodTime8StopSOC | Period 8 cutoff SOC | R/W |  |  | uint16 | %
335 | PeriodTime9StopSOC | Period 9 cutoff SOC | R/W |  |  | uint16 | %
336 | PeriodTime10StopSOC | Period 10 cutoff SOC | R/W |  |  | uint16 | %
337 | PeriodTime11StopSOC | Period 11 cutoff SOC | R/W |  |  | uint16 | %
338 | PeriodTime12StopSOC | Period 12 cutoff SOC | R/W |  |  | uint16 | %
339 | PeriodTime13StopSOC | Period 13 cutoff SOC | R/W |  |  | uint16 | %
340 | PeriodTime14StopSOC | Period 14 cutoff SOC | R/W |  |  | uint16 | %
341 | PeriodTime15StopSOC | Period 15 cutoff SOC | R/W |  |  | uint16 | %
342 | PeriodTime16StopSOC | Period 16 cutoff SOC | R/W |  |  | uint16 | %
343 | PeriodTime17StopSOC | Period 17 cutoff SOC | R/W |  |  | uint16 | %
344 | PeriodTime18StopSOC | Period 18 cutoff SOC | R/W |  |  | uint16 | %
345 | PeriodTime19StopSOC | Period 19 cutoff SOC | R/W |  |  | uint16 | %
346 | PeriodTime20StopSOC | Period 20 cutoff SOC | R/W |  |  | uint16 | %
347-374 | reserve

## input
Input Register Table
Register number | Variable Name | Detail | Data Type | Units | Comment
Group 1 |  | System operating parameter
0 | Inverter Status | Inverter running status | uint16 |  | 0x00:standby mode 0x01:Grid-connected state 0x02:Off-grid state 0x03:fault state 0x04:update mode 0x05:charging state 0x06:discharging state 0x07:bypass state
1 | PpvAll H | Total PV input power (H) | uint32 | 0.1W
2 | PpvAll L | Total PV input power (L)
3 | Vpv1 | PV1 voltage | uint16 | 0.1V
4 | PV1Curr | PV1 input current | uint16 | 0.1A
5 | 预留
6 | Ppv1 H | PV1 Input power (H) | uint32 | 0.1W
7 | Ppv1 L | PV1 Input power (L)
8 | Vpv2 | PV2 voltage | uint16 | 0.1V
9 | PV2Curr | PV2 input current | uint16 | 0.1A
10 | reserve
11 | Ppv2 H | PV2 Input power (H) | uint32 | 0.1W
12 | Ppv2 L | PV2 Input power (L)
13 | Vpv3 | PV3 voltage | uint16 | 0.1V
14 | PV3Curr | PV3 input current | uint16 | 0.1A
15 | 预留
16 | Ppv3 H | PV3 Input power (H) | uint32 | 0.1W
17 | Ppv3 L | PV3 Input power (L)
18 | Vpv4 | PV4 Voltage | uint16 | 0.1V
19 | PV4Curr | PV4 input current | uint16 | 0.1A
20 | 预留
21 | Ppv4 H | PV4 Input power (H) | uint32 | 0.1W
22 | Ppv4 L | PV4 Input power (L)
23 | SPacAll H | Total AC apparent power(H) | int32 | 0.1VA | total AC apparent power of inverter
24 | SPacAll L | Total AC apparent power(L)
25 | ActPacAll H | Total AC active power(H) | int32 | 0.1W | total AC active power of inverter
26 | ActPacAll L | Total AC active power(L)
27 | ReActPacAll H | Total AC reactive power(H) | int32 | 0.1var | total AC reactive power of inverter
28 | ReActPacAll L | Total AC reactive power(L)
29 | Vac1 | R-phase grid voltage | uint16 | 0.1V
30 | Iac1 | R-phase grid current | int16 | 0.1A | Meter current or CT current
31 | SPac1 H | R-phase apparent power (H) | int32 | 0.1VA | R-phase apparent power of inverter
32 | SPac1 L | R-phase apparent power (L)
33 | ActPac1 H | R-phase active power (H) | int32 | 0.1W | R-phase active power of inverter
34 | ActPac1 L | R-phase active power (L)
35 | ReActPac1 H | R-phase reactive power (H) | int32 | 0.1var | R-phase reactive power of inverter
36 | ReActPac1 L | R-phase reactive power (L)
37 | Vac2 | S-phase grid voltage | uint16 | 0.1V
38 | Iac2 | S-phase grid current | int16 | 0.1A | meter current
39 | SPac2 H | S-phase apparent power (H) | int32 | 0.1VA | S-phase apparent power of inverter
40 | SPac2 L | S-phase apparent power (L)
41 | ActPac2 H | S-phase active power (H) | int32 | 0.1W | S-phase active power of inverter
42 | ActPac2 L | S-phase active power (L)
43 | ReActPac2 H | S-phase reactive power (H) | int32 | 0.1var | S-phase reactive power of inverter
44 | ReActPac2 L | S-phase reactive power (L)
45 | Vac3 | T-phase grid voltage | uint16 | 0.1V
46 | Iac3 | T-phase grid current | int16 | 0.1A | meter current
47 | SPac3 H | T-phase apparent power (H) | int32 | 0.1VA | T-phase apparent power of inverter
48 | SPac3 L | T-phase apparent power (L)
49 | ActPac3 H | T-phase active power (H) | int32 | 0.1W | T-phase active power of inverter
50 | ActPac3 L | T-phase active power (L)
51 | ReActPac3 H | T-phase reactive power (H) | int32 | 0.1var | T-phase reactive power of inverter
52 | ReActPac3 L | T-phase reactive power (L)
53 | Vac_RS | RS-phase Grid line voltage | uint16 | 0.1V
54 | Vac_ST | ST-phase Grid line voltage | uint16 | 0.1V
55 | Vac_TR | TR-phase Grid line voltage | uint16 | 0.1V
56 | Fac | grid frequency | uint16 | 0.01Hz
57 | PF | power factor | int16 | 0.0001 | computational formula PF=(readValue-10000)
58 | RealOPPercent | actual output power percentage | uint16 | 1%
59 | reserve | reserve
60 | Pactouser R H | power from R phase to user (H) | uint32 | 0.1W | active power detected from R-phase meter or CT
61 | Pactouser R L | power from R phase to user (L)
62 | Pactouser S H | power from S phase to user (H) | uint32 | 0.1W | active power detected from S-phase meter or CT
63 | Pactouser S L | power from S phase to user (L)
64 | Pactouser T H | power from T phase to user (H) | uint32 | 0.1W | active power detected from T-phase meter or CT
65 | Pactouser T L | power from T phase to user (L)
66 | PactouserTotal H | Total AC power to user (H) | uint32 | 0.1W | Total active power detected from meter or CT
67 | PactouserTotal L | Total AC power to user (L)
68 | Pac to grid R H | power from AC side to the grid (H) | uint32 | 0.1W | active power detected from R-phase meter or CT
69 | Pac to grid R L | power from AC side to the grid (L)
70 | Pactogrid S H | power from AC side to the grid (H) | uint32 | 0.1W | active power detected from S-phase meter or CT
71 | Pactogrid S L | power from AC side to the grid (L)
72 | Pactogrid T H | power from AC side to the grid (H) | uint32 | 0.1W | active power detected from T-phase meter or CT
73 | Pactogrid T L | power from AC side to the grid (L)
74 | Pactogrid total H | Total power from AC side to the grid (H) | uint32 | 0.1W | Total active power detected from meter or CT
75 | Pactogrid total L | Total power from AC side to the grid (L)
76 | PLocalLoad total H | Total power from the inverter to local load (H) | uint32 | 0.1W | total load power calculated from M3
77 | PLocalLoad total L | Total power from the inverter to local load (L)
78 | EPS Fac | Off-grid frequency | uint16 | 0.01Hz
79 | EPS Vac1 | Off-grid R-phase output voltage | uint16 | 0.1V
80 | EPS Iac1 | Off-grid R-phase output current | uint16 | 0.1A
81 | EPS Pac1 H | Off-grid R-phase output Apparent Power (H) | uint32 | 0.1VA | off-grid R-phase apparent power of inverter
82 | EPS Pac1 L | Off-grid R-phase output apparent power (L)
83 | EPS ActPac1 H | Off-grid R-phase output Active Power (H) | uint32 | 0.1W | off-grid R-phase active power of inverter
84 | EPS ActPac1 L | Off-grid R-phase output active Power (L)
85 | EPS Vac2 | Off-grid S-phase output voltage | uint16 | 0.1V
86 | EPS Iac2 | Off-grid S-phase output current | uint16 | 0.1A
87 | EPS Pac2 H | Off-grid S-phase output apparent power (H) | uint32 | 0.1VA | off-grid S-phase apparent power of inverter
88 | EPS Pac2 L | Off-grid S-phase output apparent power (L)
89 | EPS ActPac2 H | Off-grid S-phase output active Power (H) | uint32 | 0.1W | off-grid S-phase active power of inverter
90 | EPS ActPac2 L | Off-grid S phase output active power (L)
91 | EPS Vac3 | Off-grid T-phase output voltage | uint16 | 0.1V
92 | EPS Iac3 | Off-grid T-phase output current | uint16 | 0.1A
93 | EPS Pac3 H | Off-grid T-phase output apparent power (H) | uint32 | 0.1VA | off-grid T-phase apparent power of inverter
94 | EPS Pac3 L | Off-grid T-phase output apparent power (H)
95 | EPS ActPac3 H | Off-grid T-phase output active Power (H) | uint32 | 0.1W | off-grid T-phase active power of inverter
96 | EPS ActPac3 L | Off-grid T-phase output active power (L)
97 | Loadpercent | off-grid output load percentage | uint16 | 1%
98 | PSystem H | System generating power H | uint32 | 0.1W | total generating power of PV and battery
99 | PSystem L | System generating power L
100 | PSelf H | Self-generated power H | uint32 | 0.1W | load power consumption of the inverter (including device consumption itself)
101 | PSelf L | Self-generated power L
102 | Pdischarge H | Battery discharge power(H) | uint32 | 0.1W
103 | Pdischarge L | Battery discharge power (L)
104 | Pcharge H | Battery charge power(H) | uint32 | 0.1W
105 | Pcharge L | Battery charge power (L)
106 | AC charge Power_H | AC Charge Power | uint32 | 0.1W
107 | AC charge Power_L | AC Charge Power
108 | CT1 Curr | CT1 sampling current | uint16 | 0.1A | It is used to be distinguished from register 30. 15KW grid current value is sampled from inverter.
109 | CT2 Curr | CT2 sampling current | uint16 | 0.1A | Used to be distinguished from register 30
110 | INV_VolR | R-phase INV voltage | uint16 | 0.1V
111 | INV_VolS | S-phase INV voltage | uint16 | 0.1V
112 | INV_VolT | T-phase INV voltage | uint16 | 0.1V
113 | INV_CurrR | R-phase INV current | uint16 | 0.1A
114 | INV_CurrS | S-phase INV current | uint16 | 0.1A
115 | INV_CurrT | T-phase INV current | uint16 | 0.1A
116 | StartDelayTime | Grid connection countdown | uint16
117 | BusUnbalanceCurr | BUS unbalanced current | int16 | 0.1A
118 | GEN_Volt | Generator voltage | uint16 | 0.1v
119 | CT_STATUS | CT insertion detection | uint16 | 1
120 | HeatPumpStatus | 3 external heat pump on/off status bit | uint16 | 1 | （1-ON，0-OFF） bit00:Heat pump 1 on/off status bit01:Heat pump 2 on/off status bit02:Heat pump 3 on/off status bit03-bit15:reserve
121 | Software sub version | Software subversion | uint16 | 1 | DSP Subversion display
122 | DryContactState | Dry contact signal connection status | uint16 | 1 | 0：Indicates that the dry contact relay is not closed 1：Indicates that the on/off of dry contact relay is for ATE test use
123 | i16Temperature_NTC_MCU | Monitor board chip temperature | Uint16 | 0.1℃
124 | i16Temperature_NTC_RIM | Monitor board environment temperature | Uint16 | 0.1℃
Group 2 | battery information
125 | Priority | Current battery priority | uint16 |  | 0:load priority 1:battery priority 2:grid priority
126 | Battery Type | Battery Type | uint16 |  | 0：lead-acid battery 1：lithium battery
127 | Vbat | battery voltage | uint16 | 0.1V
128 | SOC | The charge state of the battery | uint16 | 1%
129 | BatVolt_DSP | The inverter samples the battery voltage | uint16 | 0.1V
130 | Bus1 Voltage | Bus1 internal voltage | uint16 | 0.1V
131 | Bus2 Voltage | Bus2 internal voltage | uint16 | 0.1V
132 | Temp1 | Inverter temperature | int16 | 0.1C°
133 | Temp2 | nternal IPM temperature of the inverter | int16 | 0.1C°
134 | Temp3 | LLC Radiator temperature | int16 | 0.1C°
135 | FanSpeed | fan speed | uint16 | 1
136 | Battery Temperature | battery temperature | int16 | 0.1C°
137 | LLC Voltage | LLC voltage | uint16 | 0.1V
138 | u16BatPackVolt | Battery pack voltage | uint16 | 0.1V
139 | Systemfault word0 | system fault word0 | uint16
140 | Systemfault word1 | system fault word1 | uint16
141 | Systemfault word2 | system fault word2 | uint16
142 | Systemfault word3 | system fault word3 | uint16
143 | Systemfault word4 | system fault word4 | uint16
144 | Systemfault word5 | system fault word5 | uint16
145 | Systemfault word6 | system fault word6 | uint16
146 | Systemfault word7 | system fault word7 | uint16
147 | Fault Maincode | Inverter main fault code | uint16
148 | Fault Subcode | Inverter sub-fault code | uint16
149 | BatPower H | battery power(H) | uint32 | 0.1W
150 | BatPower L | battery power (L)
151 | reserve | reserve
152 | reserve | reserve
153 | DeratingModeFlag | deratign mode flag | uint16
154 | PowerCosFlag | leading and lagging flag | uint16
155 | BMS_Status | battery status | uint16
156 | BMS_Error1 | Battery error message 1 | uint16 |  | master battery fault
157 | BMS_Error2 | Battery error message 2 | uint16 |  | slave battery 1 fault
158 | BMS_Error3 | Battery error message 3 | uint16 |  | slave battery 2 fault
159 | BMS_WarnInfo1 | battery warning 1 | uint16 |  | master battery warning
160 | BMS_WarnInfo2 | battery warning 2 | uint16 |  | slave battery 1 warrning
161 | BMS_WarnInfo3 | battery warning 3 | uint16 |  | slave battery 2 warning
162 | BMS_SOC | battery SOC | uint16 | 1%
163 | BMS_BatteryVolt | battery voltage | uint16 | 0.1V
164 | BMS_BatteryCurr | battery current | int16 | 0.1A
165 | BMS_BatteryTemp | battery temperature | int16 | 0.1C°
166 | BMS_MaxChargeCurr | the maximum charging current the battery allows | uint16 | 0.1A
167 | BMS_MaxDischargeCurr | the maximum discharging current the battery allows | uint16 | 0.1A
168 | BMS_GaugeRM | Gauge RM | uint16 | 1Wh
169 | BMS_GaugeFCC | Gauge FCC | uint16 | 1Wh
170 | BMS_SoftVersion | software version | uint16
171 | BMS_HardVersion | hardware version | uint16
172 | BMS_DeltaVolt | single battery voltage difference | uint16 | 0.001V
173 | BMS_CycleCnt | battery Cycle Count | uint16
174 | BMS_SOH | SOH | uint16
175 | BMS_ConstantVolt | CV voltage | uint16 | 0.1V
176 | BMS_BMSInfo | BMS information | uint16
177 | BMS_PackInfo | Pack information | uint16
178 | MaxCellVol | Maximum single battery voltage | uint16 | 0.001V
179 | MinCellVol | Minimum single battery voltage | uint16 | 0.001V
180 | ModuleNum | Number of batteries in parallel | uint16
181 | CellNum | Number of cells | uint16
182 | MaxVoltCellNo | Number of maximum cell voltage | uint16
183 | MinVoltCellNo | Number of minimum cell voltage | uint16
184 | MaxTemprCell_10T | Maximum cell temperature | uint16 | 0.1C°
185 | MinTemprCell_10T | Minimum cell temperature | uint16 | 0.1C°
186 | MaxTemprCellNo | Maximum cell temperature number | uint16
187 | MinTemprCellNo | Minimum cell temperature number | uint16
188 | Protect pack ID | Faulty battery address | uint16
189 | MaxSOC | Maximum SOC in parallel | uint16 | 1%
190 | MinSOC | Minimum SOC in parallel | uint16 | 1%
191 | BMSCompany | Battery Manufacturer Information | uint16
192 | BMSFaultNo | BMS fault number | uint16
193 | uwdisChargeVolt_total | Discharge cut-off voltage of lithium battery | uint16 | 0.1V
194 | BMS_Error4 | Battery error message 1 | uint16 |  | slave battery 3 fault
195 | BMS_Error5 | Battery error message 2 | uint16 |  | slave battery 4 fault
196 | BMS_Error6 | Battery error message 3 | uint16 |  | slave battery 5 fault
197 | BMS_WarnInfo4 | Battery warning 1 | uint16 |  | slave battery 3 warning
198 | BMS_WarnInfo5 | Battery warning 2 | uint16 |  | slave battery 4 warning
199 | BMS_WarnInfo6 | Battery warning 3 | uint16 |  | slave battery 5 warning
200 | BMS_Slave1_Soft | BMS Slave battery 1 version | uint16
201 | BMS_Slave2_Soft | BMS Slave battery 2 version | uint16
202 | BMS_Slave3_Soft | BMS Slave battery 3 version | uint16
203 | BMS_Slave4_Soft | BMS Slave battery 4 version | uint16
204 | BMS_Slave5_Soft | BMS Slave battery 5 version | uint16
205 | reserve | reserve
206 | reserve | reserve
207 | BatDebuge1 | Battery BMS Debugging parameters | uint16
208 | BatDebuge2 | Battery BMS Debugging parameters | uint16
209 | BatDebuge3 | Battery BMS Debugging parameters | uint16
210 | BatDebuge4 | Battery BMS Debugging parameters | uint16
211 | BatDebuge5 | Battery BMS Debugging parameters | uint16
212 | BatDebuge6 | Battery BMS Debugging parameters | uint16
213 | BatDebuge7 | Battery BMS Debugging parameters | uint16
214 | BatDebuge8 | Battery BMS Debugging parameters | uint16
215 | BatDebuge9 | Battery BMS Debugging parameters | uint16
216 | BatDebuge10 | Battery BMS Debugging parameters | uint16
217 | Debuge1 | Master DSP Debugging parameters | uint16
218 | Debuge2 | Master DSP Debugging parameters | uint16
219 | Debuge3 | Master DSP Debugging parameters | uint16
220 | Debuge4 | Master DSP Debugging parameters | uint16
221 | Debuge5 | Master DSP Debugging parameters | uint16
222 | Debuge6 | Master DSP Debugging parameters | uint16
223 | Debuge7 | Master DSP Debugging parameters | uint16
224 | Debuge8 | Master DSP Debugging parameters | uint16
225 | Debuge9 | Slave DSP Debugging parameters | uint16
226 | Debuge10 | Slave DSP Debugging parameters | uint16
227 | Debuge11 | Slave DSP Debugging parameters | uint16
228 | Debuge12 | Slave DSP Debugging parameters | uint16
229 | Debuge13 | Slave DSP Debugging parameters | uint16
230 | Debuge14 | Slave DSP Debugging parameters | uint16
231 | Debuge15 | Slave DSP Debugging parameters | uint16
232 | Debuge16 | Slave DSP Debugging parameters | uint16
…
249 | reserve | reserve
Group 3 | Energy generation statistics
250 | Eactoday H | Daily power generation (H) | uint32 | 0.1kWh
251 | Eac today L | Daily power generation (L)
252 | Eac total H | Total power generation (H) | uint32 | 0.1kWh
253 | Eac total L | Total power generation (L)
254 | Time total H | Total working hours (H) | uint32 | 0.5s
255 | Time total L | Total working hours (L) |  | 0.5s
256 | Epv1_today H | PV1 daily energy generation (H) | uint32 | 0.1kWh
257 | Epv1_today L | PV1 daily energy generation (L)
258 | Epv1_total H | PV1 Total energy generation(H) | uint32 | 0.1kWh
259 | Epv1_total L | PV1 Total energy generation (L)
260 | Epv2_today H | PV2 daily energy generation(H) | uint32 | 0.1kWh
261 | Epv2_today L | PV2 daily energy generation(L)
262 | Epv2_total H | PV2 Total energy generation(H) | uint32 | 0.1kWh
263 | Epv2_total L | PV2 Total energy generation(L)
264 | Epv3_today H | PV3 daily energy generation(H) | uint32 | 0.1kWh
265 | Epv3_today L | PV3 daily energy generation(L)
266 | Epv3_total H | PV3 Total energy generation(H) | uint32 | 0.1kWh
267 | Epv3_total L | PV3 Total energy generation(L)
268 | Epv4_today H | PV4 daily energy generation(H) | uint32 | 0.1kWh
269 | Epv4_today L | PV4 daily energy generation(L)
270 | Epv4_total H | PV4 Total energy generation(H) | uint32 | 0.1kWh
271 | Epv4_total L | PV4 Total energy generation(L)
272 | EPVAll_Today H | PV Daily power generation (H) | uint32 | 0.1kWh
273 | EPVAll_Today L | PV Daily power generation (L)
274 | Epv_total H | PV Total energy generation(H) | uint32 | 0.1kWh
275 | Epv_total L | PV Total energy generation(L)
276 | EChargeToday H | Daily charge amount | uint32 | 0.1kWh
277 | EChargeToday L | Daily charge amount
278 | EChargeTotal H | Total charge amount | uint32 | 0.1kWh
279 | EChargeTotal L | Total charge amount
280 | EDischargeToday H | Daily discharge amount | uint32 | 0.1kWh
281 | EDischargeToday L | Daily discharge amount
282 | EDischargeTotal H | Total discharge amount | uint32 | 0.1kWh
283 | EDischargeTotal L | Total discharge amount
284 | EACharge_Today_H | daily AC charging amount（H） | uint32 | 0.1kWh
285 | EACharge_Today_L | daily AC charging amount（L）
286 | EACharge_Total_H | Total AC charging amount | uint32 | 0.1kWh
287 | EACharge_Total_L | Total AC charging amount
288 | Eextra_today H | Daily extra power from inverter to users H | uint32 | 0.1kWh
289 | Eextra_today L | Daily extra power from inverter to users L
290 | Eextra_total H | Total extra power from inverter to user H | uint32 | 0.1kWh
291 | Eextra_total L | Total extra power from inverter to user L
292 | Esystem_today H | System daily energy generation H | uint32 | 0.1kWh
293 | Esystem_ today L | System daily energy generation L
294 | Esystem_total H | System total energy generation H | uint32 | 0.1kWh
295 | Esystem_ total L | System total energy generation L
296 | Eself_today H | daily energy generation amount of self-generation and consumption H | uint32 | 0.1kWh
297 | Eself_ today L | daily energy generation amount of self-generation and consumption L
298 | Eself_total H | Total energy generation amount for self-generation and consumption H | uint32 | 0.1kWh
299 | Eself_ total L | Total energy generation amount for self-generation and consumption L
300 | Eload_today H | Daily load consumption of electricity | uint32 | 0.1kWh
301 | Eload_today L | Daily load consumption of electricity
302 | Eload_total H | Total load consumption of electricity | uint32 | 0.1kWh
303 | Eload_total L | Total load consumption of electricity
304 | EtoGrid_today H | Daily energy input to the grid | uint32 | 0.1kWh
305 | EtoGrid_today L | Daily energy input to the grid
306 | EtoGrid_total H | Total energy input to the grid | uint32 | 0.1kWh
307 | EtoGrid_total L | Total energy input to the grid
308 | EfromGrid_today H | Daily energy output from the grid | uint32 | 0.1kWh
309 | EfromGrid_today L | Daily energy output from the grid
310 | EfromGrid_total H | Total energy output from the grid | uint32 | 0.1kWh
311 | EfromGrid_total L | Total energy output from the grid
312 | DCV_R | R-phase DC voltage | int16 | 0.1V
313 | DCV_S | S-phase DC voltage | int16 | 0.1V
314 | DCV_T | T-phase DC voltage | int16 | 0.1V
315 | R_DCI | R-phase DC current | int16 | 0.1mA
316 | S_DCI | S-phase DC current | int16 | 0.1mA
317 | T_DCI | T-phase DC current | int16 | 0.1mA
318 | ISO阻值 | ISO value of resistance | uint16 | 1kΩ
319 | GFCI | ground fault circuit interrupter | int16 | 1mA
320 | bTestProcess | test process | uint16 |  | Autotest Test procedure and parameters
321 | bAutoTestStatus | test status | uint16
322 | bAutoTestStep | test step | uint16
323 | wAutoTestDefaultVFValue | Default protection value (Voltage or frequency) | uint16
324 | wAutoTestDefaultTime | Protection time | uint16
325 | wAutoTestVFNow | Actual sampling value (Voltage or frequency) | uint16
326 | wAutoTestVFVaulue | Test simulation value(Voltage or frequency) | uint16
327 | wAutoTestFaultValue | Actual protection value(Voltage or frequency) | uint16
328 | wAutoTestBreakTime | protection time | uint16
329 | DRMSFlag | Logical interface flag | uint16 | 1
330 | PVMeter_Power_R H | PV meter R-phase active power(H) | int32 | 0.1W
331 | PVMeter_Power_R L | PV meter R-phase active power(L)
332 | PVMeter_Power_S H | PV meter S-phase active power(H) | int32 | 0.1W
333 | PVMeter_Power_S L | PV meter S-phase active power(L)
334 | PVMeter_Power_T H | PV meter T-phase active power(H) | int32 | 0.1W
335 | PVMeter_Power_T L | PV meter T-phase active power(L)
336 | Parallel_Num | Number of parallel devices | uint16 | 1
337 | Parallel_ID | parallel ID | uint16 | 1
338 | Parallel_Effective_Num | Effective Number of parallel devices | uint16 | 1
339 | PVMeter_Power_ALL_H | Total active power of PV meter | int32 | 0.1W
340 | PVMeter_Power_ALL_L
341 | MasterDSP_Version | master DSP version | uint16 | 1 | main version of master DSP*100+ A subversion of the master DSP
342 | SlaveDSP_Version | slave DSP version | uint16 | 1 | main version of slave DSP*100+ A subversion of the slave DSP
343 | TotalVersion1 | Total version number 1 | uint16 | 1 | ver1 | The final form is xx.xx.xx ver1.ver2.ver3
344 | TotalVersion2 | Total version number 2 | uint16 | 1 | ver2 ver3
345 | R_DCI2 | R-phase DC current 2 | int16 | 0.1mA
346 | reserve
347 | reserve
348 | reserve
349 | reserve
350 | EPVAll_Year H | PV annual power generation H | uint32 | 0.1kWh
351 | EPVAll_Year L | PV annual power generation L
352 | Epv_Month H | PV monthly generation energy (H) | uint32 | 0.1kWh
353 | Epv_Month L | PV monthly generation energy (L)
354 | Eload_Year H | Annual load consumption of electricity | uint32 | 0.1kWh
355 | Eload_Year L | Annual load consumption of electricity
356 | Eload_Month H | Monthly load consumption of electricity | uint32 | 0.1kWh
357 | Eload_Month L | Monthly load consumption of electricity
358 | EtoGrid_Year H | Annual energy input to the grid | uint32 | 0.1kWh
359 | EtoGrid_Year L | Annual energy input to the grid
360 | EtoGrid_Month H | Monthly energy input to the grid | uint32 | 0.1kWh
361 | EtoGrid_Month L | Monthly energy input to the grid
362 | EfromGrid_Year H | Annual energy amount from the grid | uint32 | 0.1kWh
363 | EfromGrid_Year L | Annual energy amount from the grid
364 | EfromGrid_Month H | Monthly energy amount from the grid | uint32 | 0.1kWh
365 | EfromGrid_Month L | Monthly energy amount from the grid
366 | EChargeYear H | Annual charge amount | uint32 | 0.1kWh
367 | EChargeYear L | Annual charge amount
368 | EChargeTotal H | Monthly charge amount | uint32 | 0.1kWh
369 | EChargeTotal L | Monthly charge amount
370 | EDischargeYear H | Annual discharge amount | uint32 | 0.1kWh
371 | EDischargeYear L | Annual discharge amount
372 | EDischargeMonth H | Monthly discharge amount | uint32 | 0.1kWh
373 | EDischargeMonth L | Monthly discharge amount

## Appendix 1
CRC16 algorithm
const INT8U aucCRCHi[256] = { 0x00, 0xC1, 0x81, 0x40, 0x01, 0xC0, 0x80, 0x41, 0x01, 0xC0, 0x80, 0x41, 0x00, 0xC1, 0x81, 0x40, 0x01, 0xC0, 0x80, 0x41, 0x00, 0xC1, 0x81, 0x40, 0x00, 0xC1, 0x81, 0x40, 0x01, 0xC0, 0x80, 0x41, 0x01, 0xC0, 0x80, 0x41, 0x00, 0xC1, 0x81, 0x40, 0x00, 0xC1, 0x81, 0x40, 0x01, 0xC0, 0x80, 0x41, 0x00, 0xC1, 0x81, 0x40, 0x01, 0xC0, 0x80, 0x41, 0x01, 0xC0, 0x80, 0x41, 0x00, 0xC1, 0x81, 0x40, 0x01, 0xC0, 0x80, 0x41, 0x00, 0xC1, 0x81, 0x40, 0x00, 0xC1, 0x81, 0x40, 0x01, 0xC0, 0x80, 0x41, 0x00, 0xC1, 0x81, 0x40, 0x01, 0xC0, 0x80, 0x41, 0x01, 0xC0, 0x80, 0x41, 0x00, 0xC1, 0x81, 0x40, 0x00, 0xC1, 0x81, 0x40, 0x01, 0xC0, 0x80, 0x41, 0x01, 0xC0, 0x80, 0x41, 0x00, 0xC1, 0x81, 0x40, 0x01, 0xC0, 0x80, 0x41, 0x00, 0xC1, 0x81, 0x40, 0x00, 0xC1, 0x81, 0x40, 0x01, 0xC0, 0x80, 0x41, 0x01, 0xC0, 0x80, 0x41, 0x00, 0xC1, 0x81, 0x40, 0x00, 0xC1, 0x81, 0x40, 0x01, 0xC0, 0x80, 0x41, 0x00, 0xC1, 0x81, 0x40, 0x01, 0xC0, 0x80, 0x41, 0x01, 0xC0, 0x80, 0x41, 0x00, 0xC1, 0x81, 0x40, 0x00, 0xC1, 0x81, 0x40, 0x01, 0xC0, 0x80, 0x41, 0x01, 0xC0, 0x80, 0x41, 0x00, 0xC1, 0x81, 0x40, 0x01, 0xC0, 0x80, 0x41, 0x00, 0xC1, 0x81, 0x40, 0x00, 0xC1, 0x81, 0x40, 0x01, 0xC0, 0x80, 0x41, 0x00, 0xC1, 0x81, 0x40, 0x01, 0xC0, 0x80, 0x41, 0x01, 0xC0, 0x80, 0x41, 0x00, 0xC1, 0x81, 0x40, 0x01, 0xC0, 0x80, 0x41, 0x00, 0xC1, 0x81, 0x40, 0x00, 0xC1, 0x81, 0x40, 0x01, 0xC0, 0x80, 0x41, 0x01, 0xC0, 0x80, 0x41, 0x00, 0xC1, 0x81, 0x40, 0x00, 0xC1, 0x81, 0x40, 0x01, 0xC0, 0x80, 0x41, 0x00, 0xC1, 0x81, 0x40, 0x01, 0xC0, 0x80, 0x41, 0x01, 0xC0, 0x80, 0x41, 0x00, 0xC1, 0x81, 0x40 }; const INT8U aucCRCLo[256] = { 0x00, 0xC0, 0xC1, 0x01, 0xC3, 0x03, 0x02, 0xC2, 0xC6, 0x06, 0x07, 0xC7, 0x05, 0xC5, 0xC4, 0x04, 0xCC, 0x0C, 0x0D, 0xCD, 0x0F, 0xCF, 0xCE, 0x0E, 0x0A, 0xCA, 0xCB, 0x0B, 0xC9, 0x09, 0x08, 0xC8, 0xD8, 0x18, 0x19, 0xD9, 0x1B, 0xDB, 0xDA, 0x1A, 0x1E, 0xDE, 0xDF, 0x1F, 0xDD, 0x1D, 0x1C, 0xDC, 0x14, 0xD4, 0xD5, 0x15, 0xD7, 0x17, 0x16, 0xD6, 0xD2, 0x12, 0x13, 0xD3, 0x11, 0xD1, 0xD0, 0x10, 0xF0, 0x30, 0x31, 0xF1, 0x33, 0xF3, 0xF2, 0x32, 0x36, 0xF6, 0xF7, 0x37, 0xF5, 0x35, 0x34, 0xF4, 0x3C, 0xFC, 0xFD, 0x3D, 0xFF, 0x3F, 0x3E, 0xFE, 0xFA, 0x3A, 0x3B, 0xFB, 0x39, 0xF9, 0xF8, 0x38, 0x28, 0xE8, 0xE9, 0x29, 0xEB, 0x2B, 0x2A, 0xEA, 0xEE, 0x2E, 0x2F, 0xEF, 0x2D, 0xED, 0xEC, 0x2C, 0xE4, 0x24, 0x25, 0xE5, 0x27, 0xE7, 0xE6, 0x26, 0x22, 0xE2, 0xE3, 0x23, 0xE1, 0x21, 0x20, 0xE0, 0xA0, 0x60, 0x61, 0xA1, 0x63, 0xA3, 0xA2, 0x62, 0x66, 0xA6, 0xA7, 0x67, 0xA5, 0x65, 0x64, 0xA4, 0x6C, 0xAC, 0xAD, 0x6D, 0xAF, 0x6F, 0x6E, 0xAE, 0xAA, 0x6A, 0x6B, 0xAB, 0x69, 0xA9, 0xA8, 0x68, 0x78, 0xB8, 0xB9, 0x79, 0xBB, 0x7B, 0x7A, 0xBA, 0xBE, 0x7E, 0x7F, 0xBF, 0x7D, 0xBD, 0xBC, 0x7C, 0xB4, 0x74, 0x75, 0xB5, 0x77, 0xB7, 0xB6, 0x76, 0x72, 0xB2, 0xB3, 0x73, 0xB1, 0x71, 0x70, 0xB0, 0x50, 0x90, 0x91, 0x51, 0x93, 0x53, 0x52, 0x92, 0x96, 0x56, 0x57, 0x97, 0x55, 0x95, 0x94, 0x54, 0x9C, 0x5C, 0x5D, 0x9D, 0x5F, 0x9F, 0x9E, 0x5E, 0x5A, 0x9A, 0x9B, 0x5B, 0x99, 0x59, 0x58, 0x98, 0x88, 0x48, 0x49, 0x89, 0x4B, 0x8B, 0x8A, 0x4A, 0x4E, 0x8E, 0x8F, 0x4F, 0x8D, 0x4D, 0x4C, 0x8C, 0x44, 0x84, 0x85, 0x45, 0x87, 0x47, 0x46, 0x86, 0x82, 0x42, 0x43, 0x83, 0x41, 0x81, 0x80, 0x40 }; INT16U usMBCRC16( INT8U * pucFrame, INT16U usLen ) { INT16U ucCRCHi = 0xFF; INT8U ucCRCLo = 0xFF; INT16U iIndex = 0; if(pucFrame == NULL) { return 0; } while(usLen--) { iIndex = ucCRCLo ^ * pucFrame++; ucCRCLo = (INT8U)(ucCRCHi ^ aucCRCHi[iIndex]); ucCRCHi = aucCRCLo[iIndex]; } return ( ucCRCHi << 8 ¦ ucCRCLo ); }

## Appendix 2
Preaging command