## Operation Information 04
Hybrid Inverter | Name | Name-English | Address | data type | Number of bytes | Data Range | Unit | Remark | Whether to store externally Flash | modification | 0x03 | 0x04 | 0x06 | 0x10
| Protocol Header (Model Attribute Information) | [7 empty] | Save this page to ARM |  | 功能码
√ | Inverter Name | Inverter Name | 0-5 | U16*6 | 12 |  |  |  |  | Unify the writing of 16 and U16. | X | √ | X | X
√ | Inverter Type | Inverter Type | 6 | U16 | 2 |  |  | 0-99 Single-phase inverter 100-199 Three-phase inverter 200-299 Single phase hybrid Inverter（Include Split Phase hybrid Inverter） 300-399 Three Phase hybrid inverter |  |  | X | √ | X | X
√ | NormAppPower | NormAppPower | 7-8 | U32 | 4 |  | 1W |  |  | 1. Change 1w to 1VA; 2. Change the rated apparent power to the rated power, unit: 1VA to 1W | X | √ | X | X
√ | NormReactPower | NormReactPower | 9-10 | U32 | 4 |  | 1var |  |  |  | X | √ | X | X
√ | HardName | HardName | 11-14 | U16*4 | 8 | ASCII |  |  |  |  | X | √ | X | X
√ | HardVer | HardVer | 15 | U16 | 2 | [5 empty] | X | √ | X | X
√ | ProtocolName | ProtocolName | 16-19 | U16*4 | 8 | ASCII |  | “” |  |  | X | √ | X | X
√ | ProtocolVer | ProtocolVer | 20 | U16 | 2 |  |  | XXX.XX |  | Starting from 1 | X | √ | X | X
√ | MasterName | MasterName | 21-24 | U16*4 | 8 | ASCII |  |  |  |  | X | √ | X | X
√ | MasterVer | MasterVer | 25 | U16 | 2 |  |  | XXX.XX |  |  | X | √ | X | X
√ | SlaveName | SlaveName | 26-29 | U16*4 | 8 | ASCII |  |  |  |  | X | √ | X | X
√ | SlaveVer | SlaveVer | 30 | U16 | 2 |  |  | XXX.XX |  |  | X | √ | X | X
√ | HMIName | HMIName | 31-34 | U16*4 | 8 | ASCII |  |  |  |  | X | √ | X | X
√ | HMIVer | HMIVer | 35 | U16 | 2 |  |  | XXX.XX |  |  | X | √ | X | X
√ | CPLDName | CPLDName | 36-39 | U16*4 | 8 | ASCII |  |  |  |  | X | √ | X | X
√ | CPLDVer | CPLDVer | 40 | U16 | 2 |  |  | XXX.XX |  |  | X | √ | X | X
√ | Inverter SN | SerialNumber15-14 | 41 | U16 | 2 | ASCII |  |  |  |  | X | √ | X | X
√ |  | SerialNumber13-12 | 42 | U16 | 2 | ASCII |  |  |  |  | X | √ | X | X
√ |  | SerialNumber11-10 | 43 | U16 | 2 | ASCII |  |  |  |  | X | √ | X | X
√ |  | SerialNumber9-8 | 44 | U16 | 2 | ASCII |  |  |  |  | X | √ | X | X
√ |  | SerialNumber7-6 | 45 | U16 | 2 | ASCII |  |  |  |  | X | √ | X | X
√ |  | SerialNumber5-4 | 46 | U16 | 2 | ASCII |  |  |  |  | X | √ | X | X
√ |  | SerialNumber3-2 | 47 | U16 | 2 | ASCII |  |  |  |  | X | √ | X | X
√ |  | SerialNumber1-0 | 48 | U16 | 2 | ASCII |  |  |  |  | X | √ | X | X
√ | 国家Safty | CountrySafty | 49 | U16 | 2 | 安规 |  |  |  |  | X | √ | X | X
√ | MaxAcOutCurr | MaxAcOutCurr | 50-51 | U32 | 4 |  | 0.01A |  |  | New unit added 0.01A | X | √ | X | X
√ | InverCharacter | InverCharacter | 52-53 | U32 | 4 |  |  | B0-B2: 0 represents grid connected machine, 1 represents low-voltage energy storage, and 2 represents high-voltage energy storage; B3-B5: 0 represents single-phase, 1 represents split phase, and 2 represents three-phase; B6-B9: PV boost routes, where 0 represents 1 route, 1 represents 2 routes, and N represents N+routes; B10:0 represents no generator, 1 represents generator present; B11-B31: reserved; |  | Added 21.05.12 for platform recognition B1-B31 changed to B11-B31 | X | √ | X | X
| Reserve | Reserve | 54-499 | [7 empty] | X | √ | X | X
| Real time operation information 1 (PV+grid connected operation information) | [9 empty] | X | √ | X | X
√ | Bus voltage | Vbus | 500 | U16 | 2 |  | 0.1V | If it is single-phase, only the R-phase voltage and R-phase current are effective; If it is two phases, only the voltage and current of R and S phases are effective; If the three-phase four wire system is used, it means "X-phase voltage"; If the three-phase three wire system is used, it means "x - X-ray voltage" Positive indicates the inverter is supplying power to the grid, negative indicates the inverter is taking power from the grid |  |  | X | √ | X | X
√ | Negative bus voltage | Vnbus | 501 | U16 | 2 |  | 0.1V |  |  |  | X | √ | X | X
√ | Insulation impedance value | Riso | 502 | U16 | 2 |  | KΩ |  |  |  | X | √ | X | X
√ | Effective value of leakage current | IgfciRms | 503 | U16 | 2 |  | 1mA |  |  |  | X | √ | X | X
√ | R-phase DC component | DCIR | 504 | S16 | 2 |  | 1mA |  |  |  | X | √ | X | X
√ | S-phase DC component | DCIS | 505 | S16 | 2 |  | 1mA |  |  |  | X | √ | X | X
√ | T-phase DC component | DCIT | 506 | S16 | 2 |  | 1mA |  |  |  | X | √ | X | X
√ | R-phase grid voltage | VgridR | 507 | U16 | 2 |  | 0.1V |  |  |  | X | √ | X | X
√ | S-phase grid voltage | VgridS | 508 | U16 | 2 |  | 0.1V |  |  |  | X | √ | X | X
√ | T-phase grid voltage | VgridT | 509 | U16 | 2 |  | 0.1V |  |  |  | X | √ | X | X
√ | R-phase inverter current | IinvR | 510 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | S-phase inverter current | IinvS | 511 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | T-phase inverter current | IinvT | 512 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | R-phase grid frequency | FgridR | 513 | U16 | 2 |  | 0.01Hz |  |  |  | X | √ | X | X
√ | S-phase grid frequency | FgridS | 514 | U16 | 2 |  | 0.01Hz |  |  |  | X | √ | X | X
√ | T-phase grid frequency | FgridT | 515 | U16 | 2 |  | 0.01Hz |  |  |  | X | √ | X | X
√ | A-phase active power | PinvR | 516-517 | S32 | 4 |  | W |  |  |  | X | √ | X | X
√ | B-phase active power | PinvS | 518-519 | S32 | 4 |  | W |  |  |  | X | √ | X | X
√ | C-phase active power | PinvT | 520-521 | S32 | 4 |  | W |  |  |  | X | √ | X | X
√ | Total active power | Pinv | 522-523 | S32 | 4 |  | W |  |  |  | X | √ | X | X
√ | Total reactive power | Qinv | 524-525 | S32 | 4 |  | W |  |  |  | X | √ | X | X
√ | Total power factor | PFinv | 526 | S16 | 2 |  | 0.001 |  |  |  | X | √ | X | X
√ | Total apparent power | Sinv | 527-528 | U32 | 4 |  | VA |  |  |  | X | √ | X | X
√ | R-phase grid connected power (electricity meter) | PgridR | 529-530 | S32 | 4 |  | W | Positive indicates the inverter is supplying power to the grid, negative indicates the inverter is taking power from the grid |  |  | X | √ | X | X
√ | S-phase grid connected power (electricity meter) | PgridS | 531-532 | S32 | 4 |  | W |  |  |  | X | √ | X | X
√ | T-phase grid connected power (electricity meter) | PgridT | 533-534 | S32 | 4 |  | W |  |  |  | X | √ | X | X
√ | Total grid connected active power | Pgrid | 535-536 | S32 | 4 |  | W |  |  | New unit added W | X | √ | X | X
√ | Total grid connected reactive power | Qgrid | 537-538 | S32 | 4 |  | Var |  |  | New unit added Var | X | √ | X | X
√ | Total parallel network viewing power | Sgrid | 539-540 | U32 | 4 |  | VA |  |  | New unit added VA | X | √ | X | X
× | R-Phase负载Power | PloadR | 541-542 | S32 | 4 |  | W |  |  |  | X | √ | X | X
× | S-Phase负载Power | PloadS | 543-544 | S32 | 4 |  | W |  |  |  | X | √ | X | X
× | T-Phase负载Power | PloadT | 545-546 | S32 | 4 |  | W |  |  |  | X | √ | X | X
√ | Total load active power | Pload | 547-548 | S32 | 4 |  | W |  |  | New unit added W | X | √ | X | X
× | Total负载无功Power | Qload | 549-550 | S32 | 4 |  | Var |  |  | New unit added Var | X | √ | X | X
× | Total负载视在Power | Sload | 551-552 | U32 | 4 |  | VA |  |  | New unit added VA | X | √ | X | X
√ | PV total power | Ppv | 553-554 | U32 | 4 |  | W |  |  | New unit added W | X | √ | X | X
√ | PV1 Voltage | Vpv1 | 555 | U16 | 2 |  | 0.1V |  |  |  | X | √ | X | X
√ | PV1Current | Ipv1 | 556 | U16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | PV1Power | Ppv1 | 557 | U16 | 2 |  | W |  |  |  | X | √ | X | X
√ | PV2Voltage | Vpv2 | 558 | U16 | 2 |  | 0.1V |  |  |  | X | √ | X | X
√ | PV2Current | Ipv2 | 559 | U16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | PV2Power | Ppv2 | 560 | U16 | 2 |  | W |  |  |  | X | √ | X | X
√ | PV3Voltage | Vpv3 | 561 | U16 | 2 |  | 0.1V |  |  |  | X | √ | X | X
√ | PV3Current | Ipv3 | 562 | U16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | PV3Power | Ppv3 | 563 | U16 | 2 |  | W |  |  |  | X | √ | X | X
√ | PV4Voltage | Vpv4 | 564 | U16 | 2 |  | 0.1V |  |  |  | X | √ | X | X
√ | PV4Current | Ipv4 | 565 | U16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | PV4Power | Ppv4 | 566 | U16 | 2 |  | W |  |  |  | X | √ | X | X
√ | PV5Voltage | Vpv5 | 567 | U16 | 2 |  | 0.1V |  |  |  | X | √ | X | X
√ | PV5Current | Ipv5 | 568 | U16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | PV5Power | Ppv5 | 569 | U16 | 2 |  | W |  |  |  | X | √ | X | X
√ | PV6Voltage | Vpv6 | 570 | U16 | 2 |  | 0.1V |  |  |  | X | √ | X | X
√ | PV6Current | Ipv6 | 571 | U16 | 2 |  | 0.01A |  |  | For hybid invter, the total PV power is required | X | √ | X | X
√ | PV6Power | Ppv6 | 572 | U16 | 2 |  | W |  |  |  | X | √ | X | X
√ | PVConnection status | PVConn | 573 | U16 | 2 | B0:CONNECTED B1:AVAILABLE B2:OPERATING B3:TEST |  |  |  |  | X | √ | X | X
| Reserve | Reserve | 574-999 | [7 empty] | X | √ | X | X
| Real-time operating information 2 (PV + grid-connected power generation) | [9 empty] | X | √ | X | X
× | The daily power generation of the inverter | EInvOutDay | 1000 | U16 | 2 |  | 0.1kwh |  | 存 | 单位0.1wh修改为0.1kwh | X | √ | X | X
× | transformerSame day从power grid 取电量 | EInvRecDay | 1001 | U16 | 2 |  | 0.1kwh |  | 存 |  | X | √ | X | X
√ | The amount of electricity delivered to the grid on the same day | EtogridDay | 1002 | U16 | 2 |  | 0.1kwh |  | 存 |  | X | √ | X | X
√ | The amount of electricity taken from the power grid on the same day | EfromgridDay | 1003 | U16 | 2 |  | 0.1kwh |  |  |  | X | √ | X | X
√ | The electricity consumption from the current day to the load | EtoLoadDay | 1004 | U16 | 2 |  | 0.1kwh |  | 存 |  | X | √ | X | X
× | Same day取负载的电量 | EfromLoadDay | 1005 | U16 | 2 |  | 0.1kwh |  |  |  | X | √ | X | X
√ | Daily PVpower generation | EPVDay | 1006-1007 | U32 | 4 |  | 0.1kwh |  | 存 |  | X | √ | X | X
√ | Daily PV1power generation | EPV1Day | 1008 | U16 | 2 |  | 0.1kwh |  | 存 |  | X | √ | X | X
√ | Daily PV2power generation | EPV2Day | 1009 | U16 | 2 |  | 0.1kwh |  | 存 |  | X | √ | X | X
√ | Daily PV3power generation | EPV3Day | 1010 | U16 | 2 |  | 0.1kwh |  | 存 |  | X | √ | X | X
√ | Daily PV4power generation | EPV4Day | 1011 | U16 | 2 |  | 0.1kwh |  | 存 |  | X | √ | X | X
√ | Daily PV5power generation | EPV5Day | 1012 | U16 | 2 |  | 0.1kwh |  | 存 |  | X | √ | X | X
√ | Daily PV6power generation | EPV6Day | 1013 | U16 | 2 |  | 0.1kwh |  | 存 |  | X | √ | X | X
× | Total power generation of inverters | EInvOutTotal | 1014-1015 | U32 | 4 |  | 0.1kwh |  | 存 |  | X | √ | X | X
× | transformerTotal从power grid 取电量 | EInvRecTotal | 1016-1017 | U32 | 4 |  | 0.1kwh |  | 存 |  | X | √ | X | X
√ | Total electricity to the grid | EtogridTotal | 1018-1019 | U32 | 4 |  | 0.1kwh |  | 存 |  | X | √ | X | X
√ | Total electricity consumption from the power grid | EfromgridTotal | 1020-1021 | U32 | 4 |  | 0.1kwh |  |  |  | X | √ | X | X
√ | Total power to load | EtoLoadTotal | 1022-1023 | U32 | 4 |  | 0.1kwh |  | 存 |  | X | √ | X | X
× | Total取负载的电量 | EfromLoadTotal | 1024-1025 | U32 | 4 |  | 0.1kwh |  |  |  | X | √ | X | X
√ | Total PV power generation | EPVTotal | 1026-1027 | U32 | 4 |  | 0.1kwh |  | 存 |  | X | √ | X | X
| Reserve | Reserve | 1028-1499 | [7 empty] | X | √ | X | X
| Real-time operation information 3 (Backup operation information) | [9 empty] | X | √ | X | X
√ | R-phase Voltage DC component | DCVR | 1500 | S16 | 2 |  | mV | If the output type is 0, only phase A voltage and phase A electrical current are valid; If the output type is 1, it means: "X-phase voltage"; If the output type is 2, it means: "x-x line voltage". |  | New unit added mV | X | √ | X | X
√ | S-phase Voltage DC component | DCVS | 1501 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | S-phase Voltage DC component | DCVT | 1502 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | R-phase EPSVoltage | VepsR | 1503 | U16 | 2 |  | 0.1V |  |  |  | X | √ | X | X
√ | S-PhaseEPSVoltage | VepsS | 1504 | U16 | 2 |  | 0.1V |  |  |  | X | √ | X | X
√ | T-PhaseEPSVoltage | VepsT | 1505 | U16 | 2 |  | 0.1V |  |  |  | X | √ | X | X
√ | R-PhaseEPSCurrent | IepsR | 1506 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | S-PhaseEPSCurrent | IepsS | 1507 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | T-PhaseEPSCurrent | IepsT | 1508 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | R-PhaseEPSCurrent | FepsR | 1509 | U16 | 2 |  | 0.01Hz |  |  |  | X | √ | X | X
√ | R-PhaseEPSPower | PepsR | 1510 | S16 | 2 |  | W |  |  |  | X | √ | X | X
√ | S-PhaseEPSPower | PepsS | 1511 | S16 | 2 |  | W |  |  |  | X | √ | X | X
√ | T-PhaseEPSPower | PepsT | 1512 | S16 | 2 |  | W |  |  |  | X | √ | X | X
√ | Total PSPower | Peps | 1513-1514 | S32 | 4 |  | W |  |  | When connected in off-grid parallel connection, active power and reactive power may also be negative values, and the relevant ones should be changed to signed numbers.。 | X | √ | X | X
√ | TotalEPSNoPower | Qeps | 1515-1516 | S32 | 4 |  | Var |  |  | VA修改为Var | X | √ | X | X
√ | TotalEPSPower | Seps | 1517-1518 | U32 | 4 |  | VA |  |  |  | X | √ | X | X
√ | Same dayEPSDischarge capacity | EepsInvDay | 1519 | U16 | 2 |  | 0.1kwh |  | 存 |  | X | √ | X | X
√ | Same dayEPSCharging capacity | EepsRecDay | 1520 | U16 | 2 |  | 0.1kwh |  | 存 |  | X | √ | X | X
√ | R-PhaseGENVoltage | VgenR | 1521 | U16 | 2 |  | 0.1V |  |  | New unit added 0.1V | X | √ | X | X
√ | S-PhaseGENVoltage | VgenS | 1522 | U16 | 2 |  | 0.1V |  |  |  | X | √ | X | X
√ | T-PhaseGENVoltage | VgenT | 1523 | U16 | 2 |  | 0.1V |  |  |  | X | √ | X | X
√ | R-PhaseGENCurrent | IgenR | 1524 | S16 | 2 |  | 0.01A |  |  | New unit added 0.01A | X | √ | X | X
√ | S-PhaseGENCurrent | IgenS | 1525 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | T-PhaseGENCurrent | IgenT | 1526 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | R-PhaseGEN Power | PgenR | 1527 | S16 | 2 |  | W |  |  | New unit added W | X | √ | X | X
√ | S-PhaseGENPower | PgenS | 1528 | S16 | 2 |  | W |  |  |  | X | √ | X | X
√ | T-PhaseGENPower | PgenT | 1529 | S16 | 2 |  | W |  |  |  | X | √ | X | X
√ | TotalGENPower | Pgen | 1530-1531 | S32 | 4 |  | W |  |  |  | X | √ | X | X
√ | TotalGEN no Power | Qgen | 1532-1533 | S32 | 4 |  | Var |  |  | New unit added Var | X | √ | X | X
√ | TotalGENPower | Sgen | 1534-1535 | U32 | 4 |  | VA |  |  | New unit added VA | X | √ | X | X
√ | Same dayGENPower generation | EgenDay | 1536 | U16 | 2 |  | 0.1kwh |  |  | New unit added 0.1kwh | X | √ | X | X
√ | TotalEPSDischarge capacity | EepsInvTotal | 1537-1538 | U32 | 4 |  | 0.1kwh |  |  |  | X | √ | X | X
√ | TotalEPSCharging capacity | EepsRecTotal | 1539-1540 | U32 | 4 |  | 0.1kwh |  |  |  | X | √ | X | X
√ | TotalGENPower generation | EgenTotal | 1541-1542 | U32 | 4 |  | 0.1kwh |  |  |  | X | √ | X | X
| Reserve | Reserve | 1543-1999 | [7 empty] | X | √ | X | X
| Real-time operating information 4 (battery operating information) | [9 empty] | X | √ | X | X
√ | Battery State | BatState | 2000 | U16 | 2 |  |  | No battery 0 Fault 1 Sleep 2 Start 3 Charging 4 Discharge 5 OFF 6 Wake Up 7 |  | Excludes forced charging | X | √ | X | X
√ | Batterytemperature | Tbat | 2001 | s16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | Battery（SOC） | SOC | 2002 | U16 | 2 |  | % |  |  |  | X | √ | X | X
√ | Battery health status (SOH) | SOH | 2003 | U16 | 2 |  | % |  |  |  | X | √ | X | X
√ | BatteryVoltage | Vbat | 2004 | U16 | 2 |  | 0.1V |  |  |  | X | √ | X | X
√ | BatteryCurrent | Ibat | 2005 | S16 | 2 |  | 0.01A | Positive means the battery is discharged Negative means the battery is charged |  |  | X | √ | X | X
√ | BuckBoostVoltage | Vbb | 2006 | U16 | 2 |  | 0.1V |  |  |  | X | √ | X | X
√ | BatteryTotalPower | Pbat | 2007-2008 | S32 | 4 |  | 1W | Positive means the battery is discharged Negative means the battery is charged |  | 1. Change to signed number, 2. Unit 0.1V changed to 1W | X | √ | X | X
√ | BatterySame dayCharging capacity | EChgDay | 2009 | U16 | 2 |  | 0.1kwh |  | 存 | Unit 0.1wh changed to 0.1kwh | X | √ | X | X
√ | BatterySame dayDischarge capacity | EDischgDay | 2010 | U16 | 2 |  | 0.1kwh |  | 存 |  | X | √ | X | X
√ | TotalBatteryCharging capacity | EChgTotal | 2011-2012 | U32 | 4 |  | 0.1kwh |  |  | New unit added 0.1kwh | X | √ | X | X
√ | TotalBatteryDischarge capacity | EDischgTotal | 2013-2014 | U32 | 4 |  | 0.1kwh |  |  | New unit added 0.1kwh | X | √ | X | X
√ | Battery control command | BatCtrlCmd | 2015 | U16 | 2 |  |  | bit0-1: 0-no operation, 1-high voltage power on, 2-high voltage power off bit2: charging bit3: discharge bit4:restart bit5: shutdown bit6-15: reserved |  |  | X | √ | X | X
√ | BatteryConnection status | StorConn | 2016 | U16 | 2 | B0:CONNECTED B1:AVAILABLE B2:OPERATING B3:TEST |  |  |  |  | X | √ | X | X
| Reserve | Reserve | 2017-2499 | [7 empty] | X | √ | X | X
| Real-time operation information 5 (system information) | [9 empty] | X | √ | X | X
√ | running state | RunState | 2500 | U16 | 2 |  |  | Initial power on 0 Standby 1 Start 2 Grid 3 Off-grid 4 DG 5 From grid to off-grid 6 From Off-grid to grid 7 Power failure processing 8 Shutdown 9 Fault 10 Upgrading 11 Aging 12 Open loop 13 Sampling calibration 14 |  |  | X | √ | X | X
√ | Current triggering limit Power mode | PLimitMode | 2501-2502 | U32 | 4 |  |  | 0x0000 unlimited power 0x0001 Temperature limit power 0x0002 Manually set power limit 0x0004 Grid voltage and PF power limit 0x0008 Over frequency power limit 0x0010 Individual PV2 input power limit 0x0020 Fault recovery slow start power limit 0x0040 reserved channel |  | Specific power limiting methods can be added, but it is recommended to leave U32. | X | √ | X | X
√ | Current triggering of power grid dispatch mode | GridCrlMode | 2503-2504 | U32 | 4 |  |  | 0 E_GRID_ADJUST_DEF 1 E_GRID_ADJUST_LVRT 2 E_GRID_ADJUST_FIXE, 3 E_GRID_ADJUST_PF 4 E_GRID_ADJUST_QP 5 E_GRID_ADJUST_TEST |  | It should be presented bit by bit, and several combinations may appear at the same time. It is recommended to leave U32. | X | √ | X | X
√ | PV1MPPT working mode | PV1MpptMode | 2505 | U16 | 2 |  |  | 0 default value 1 standby 2 Boost scan 3 Bus scan 4 Boost MPPT operation 5 Bus MPPT operation 6 Centralized Bus operation |  |  | X | √ | X | X
√ | PV2MPPT working mode | PV2MpptMode | 2506 | U16 | 2 | [5 empty] | X | √ | X | X
√ | PV3MPPT working mode | PV3MpptMode | 2507 | U16 | 2 | [5 empty] | X | √ | X | X
√ | PV4MPPT working mode | PV4MpptMode | 2508 | U16 | 2 | [5 empty] | X | √ | X | X
√ | PV5MPPT working mode | PV5MpptMode | 2509 | U16 | 2 | [5 empty] | X | √ | X | X
√ | PV6MPPT working mode | PV6MpptMode | 2510 | U16 | 2 | [5 empty] | X | √ | X | X
√ | Adjustable load DO status | LoadCtrlState | 2511 | U16 | 2 | [5 empty] | X | √ | X | X
√ | Active detection status of electric meter | MeterTestState | 2512 | U16 | 2 | [5 empty] | X | √ | X | X
√ | Start time | ConncetTime | 2513 | U16 | 2 |  | S |  |  |  | X | √ | X | X
√ | Internal temperature of inverter temperature | Tinner | 2514 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | transformertemperature | Ttransf | 2515 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | temperature1 | Temp1 | 2516 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | temperature2 | Temp2 | 2517 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
| Reserve | Reserve | 2518-2999 | [7 empty] | X | √ | X | X
| Real-time operating information 6 (faults and alarms) | [9 empty] | X | √ | X | X
√ | PVfault1 | PvErr1 | 3000-3001 | U32 | 4 | [5 empty] | X | √ | X | X
√ | PVfault2 | PvErr2 | 3002-3003 | U32 | 4 | [5 empty] | X | √ | X | X
√ | Batteryfault1 | BatErr1 | 3004-3005 | U32 | 4 | [5 empty] | X | √ | X | X
√ | Batteryfault2 | BatErr2 | 3006-3007 | U32 | 4 | [5 empty] | X | √ | X | X
√ | power grid fault | GridErr | 3008-3009 | U32 | 4 | [5 empty] | X | √ | X | X
√ | Off- grid fault | OffGridErr | 3010-3011 | U32 | 4 | [5 empty] | X | √ | X | X
√ | DC sidefault1 | DCErr1 | 3012-3013 | U32 | 4 | [5 empty] | X | √ | X | X
√ | DC sidefault2 | DCErr2 | 3014-3015 | U32 | 4 | [5 empty] | X | √ | X | X
√ | AC sidefault | ACErr | 3016-3017 | U32 | 4 | [5 empty] | X | √ | X | X
√ | systemfault1 | SysErr1 | 3018-3019 | U32 | 4 | [5 empty] | X | √ | X | X
√ | systemfault2 | SysErr2 | 3020-3021 | U32 | 4 | [5 empty] | X | √ | X | X
√ | permanent fault | PermErr | 3022-3023 | U32 | 4 | [5 empty] | X | √ | X | X
√ | Internal alarm | InWarning | 3024-3025 | U32 | 4 | [5 empty] | X | √ | X | X
√ | external alarm | OutWarning | 3026-3027 | U32 | 4 | [5 empty] | X | √ | X | X
| Reserve | Reserve | 3028-3499 | [7 empty] | X | √ | X | X
| Cell data | [9 empty] | X | √ | X | X
√ | cell1data-Voltage | BC1_U | 5000 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell1data-Current | BC1_I | 5001 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell1data-temperature | BC1_T | 5002 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell1data-Soc | BC1_SOC | 5003 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell2data-Voltage | BC2_U | 5004 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell2data-Current | BC2_I | 5005 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell2data-temperature | BC2_T | 5006 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell2data-Soc | BC2_SOC | 5007 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell3data-Voltage | BC3_U | 5008 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell3data-Current | BC3_I | 5009 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell3data-temperature | BC3_T | 5010 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell3data-Soc | BC3_SOC | 5011 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell4data-Voltage | BC4_U | 5012 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell4data-Current | BC4_I | 5013 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell4data-temperature | BC4_T | 5014 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell4data-Soc | BC4_SOC | 5015 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell5data-Voltage | BC5_U | 5016 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell5data-Current | BC5_I | 5017 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell5data-temperature | BC5_T | 5018 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell5data-Soc | BC5_SOC | 5019 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell6data-Voltage | BC6_U | 5020 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell6data-Current | BC6_I | 5021 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell6data-temperature | BC6_T | 5022 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell6data-Soc | BC6_SOC | 5023 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell7data-Voltage | BC7_U | 5024 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell7data-Current | BC7_I | 5025 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell7data-temperature | BC7_T | 5026 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell7data-Soc | BC7_SOC | 5027 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell8data-Voltage | BC8_U | 5028 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell8data-Current | BC8_I | 5029 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell8data-temperature | BC8_T | 5030 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell8data-Soc | BC8_SOC | 5031 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell9data-Voltage | BC9_U | 5032 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell9data-Current | BC9_I | 5033 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell9data-temperature | BC9_T | 5034 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell9data-Soc | BC9_SOC | 5035 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell10data-Voltage | BC10_U | 5036 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell10data-Current | BC10_I | 5037 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell10data-temperature | BC10_T | 5038 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell10data-Soc | BC10_SOC | 5039 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell11data-Voltage | BC11_U | 5040 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell11data-Current | BC11_I | 5041 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell11data-temperature | BC11_T | 5042 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell11data-Soc | BC11_SOC | 5043 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell12data-Voltage | BC12_U | 5044 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell12data-Current | BC12_I | 5045 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell12data-temperature | BC12_T | 5046 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell12data-Soc | BC12_SOC | 5047 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell13data-Voltage | BC13_U | 5048 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell13data-Current | BC13_I | 5049 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell13data-temperature | BC13_T | 5050 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell13data-Soc | BC13_SOC | 5051 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell14data-Voltage | BC14_U | 5052 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell14data-Current | BC14_I | 5053 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell14data-temperature | BC14_T | 5054 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell14data-Soc | BC14_SOC | 5055 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell15data-Voltage | BC15_U | 5056 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell15data-Current | BC15_I | 5057 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell15data-temperature | BC15_T | 5058 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell15data-Soc | BC15_SOC | 5059 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell16data-Voltage | BC16_U | 5060 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell16data-Current | BC16_I | 5061 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell16data-temperature | BC16_T | 5062 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell16data-Soc | BC16_SOC | 5063 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell17data-Voltage | BC17_U | 5064 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell17data-Current | BC17_I | 5065 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell17data-temperature | BC17_T | 5066 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell17data-Soc | BC17_SOC | 5067 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell18data-Voltage | BC18_U | 5068 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell18data-Current | BC18_I | 5069 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell18data-temperature | BC18_T | 5070 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell18data-Soc | BC18_SOC | 5071 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell19data-Voltage | BC19_U | 5072 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell19data-Current | BC19_I | 5073 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell19data-temperature | BC19_T | 5074 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell19data-Soc | BC19_SOC | 5075 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell20data-Voltage | BC20_U | 5076 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell20data-Current | BC20_I | 5077 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell20data-temperature | BC20_T | 5078 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell20data-Soc | BC20_SOC | 5079 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell21data-Voltage | BC21_U | 5080 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell21data-Current | BC21_I | 5081 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell21data-temperature | BC21_T | 5082 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell21data-Soc | BC21_SOC | 5083 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell22data-Voltage | BC22_U | 5084 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell22data-Current | BC22_I | 5085 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell22data-temperature | BC22_T | 5086 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell22data-Soc | BC22_SOC | 5087 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell23data-Voltage | BC23_U | 5088 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell23data-Current | BC23_I | 5089 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell23data-temperature | BC23_T | 5090 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell23data-Soc | BC23_SOC | 5091 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell24data-Voltage | BC24_U | 5092 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell24data-Current | BC24_I | 5093 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell24data-temperature | BC24_T | 5094 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell24data-Soc | BC24_SOC | 5095 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell25data-Voltage | BC25_U | 5096 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell25data-Current | BC25_I | 5097 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell25data-temperature | BC25_T | 5098 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell25data-Soc | BC25_SOC | 5099 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell26data-Voltage | BC26_U | 5100 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell26data-Current | BC26_I | 5101 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell26data-temperature | BC26_T | 5102 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell26data-Soc | BC26_SOC | 5103 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell27data-Voltage | BC27_U | 5104 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell27data-Current | BC27_I | 5105 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell27data-temperature | BC27_T | 5106 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell27data-Soc | BC27_SOC | 5107 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell28data-Voltage | BC28_U | 5108 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell28data-Current | BC28_I | 5109 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell28data-temperature | BC28_T | 5110 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell28data-Soc | BC28_SOC | 5111 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell29data-Voltage | BC29_U | 5112 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell29data-Current | BC29_I | 5113 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell29data-temperature | BC29_T | 5114 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell29data-Soc | BC29_SOC | 5115 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell30data-Voltage | BC30_U | 5116 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell30data-Current | BC30_I | 5117 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell30data-temperature | BC30_T | 5118 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell30data-Soc | BC30_SOC | 5119 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell31data-Voltage | BC31_U | 5120 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell31data-Current | BC31_I | 5121 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell31data-temperature | BC31_T | 5122 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell31data-Soc | BC31_SOC | 5123 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell32data-Voltage | BC32_U | 5124 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell32data-Current | BC32_I | 5125 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell32data-temperature | BC32_T | 5126 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell32data-Soc | BC32_SOC | 5127 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell33data-Voltage | BC33_U | 5128 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell33data-Current | BC33_I | 5129 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell33data-temperature | BC33_T | 5130 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell33data-Soc | BC33_SOC | 5131 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell34data-Voltage | BC34_U | 5132 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell34data-Current | BC34_I | 5133 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell34data-temperature | BC34_T | 5134 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell34data-Soc | BC34_SOC | 5135 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell35data-Voltage | BC35_U | 5136 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell35data-Current | BC35_I | 5137 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell35data-temperature | BC35_T | 5138 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell35data-Soc | BC35_SOC | 5139 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell36data-Voltage | BC36_U | 5140 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell36data-Current | BC36_I | 5141 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell36data-temperature | BC36_T | 5142 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell36data-Soc | BC36_SOC | 5143 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell37data-Voltage | BC37_U | 5144 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell37data-Current | BC37_I | 5145 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell37data-temperature | BC37_T | 5146 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell37data-Soc | BC37_SOC | 5147 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell38data-Voltage | BC38_U | 5148 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell38data-Current | BC38_I | 5149 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell38data-temperature | BC38_T | 5150 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell38data-Soc | BC38_SOC | 5151 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell39data-Voltage | BC39_U | 5152 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell39data-Current | BC39_I | 5153 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell39data-temperature | BC39_T | 5154 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell39data-Soc | BC39_SOC | 5155 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell40data-Voltage | BC40_U | 5156 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell40data-Current | BC40_I | 5157 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell40data-temperature | BC40_T | 5158 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell40data-Soc | BC40_SOC | 5159 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell41data-Voltage | BC41_U | 5160 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell41data-Current | BC41_I | 5161 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell41data-temperature | BC41_T | 5162 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell41data-Soc | BC41_SOC | 5163 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell42data-Voltage | BC42_U | 5164 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell42data-Current | BC42_I | 5165 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell42data-temperature | BC42_T | 5166 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell42data-Soc | BC42_SOC | 5167 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell43data-Voltage | BC43_U | 5168 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell43data-Current | BC43_I | 5169 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell43data-temperature | BC43_T | 5170 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell43data-Soc | BC43_SOC | 5171 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell44data-Voltage | BC44_U | 5172 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell44data-Current | BC44_I | 5173 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell44data-temperature | BC44_T | 5174 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell44data-Soc | BC44_SOC | 5175 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell45data-Voltage | BC45_U | 5176 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell45data-Current | BC45_I | 5177 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell45data-temperature | BC45_T | 5178 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell45data-Soc | BC45_SOC | 5179 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell46data-Voltage | BC46_U | 5180 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell46data-Current | BC46_I | 5181 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell46data-temperature | BC46_T | 5182 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell46data-Soc | BC46_SOC | 5183 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell47data-Voltage | BC47_U | 5184 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell47data-Current | BC47_I | 5185 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell47data-temperature | BC47_T | 5186 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell47data-Soc | BC47_SOC | 5187 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell48data-Voltage | BC48_U | 5188 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell48data-Current | BC48_I | 5189 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell48data-temperature | BC48_T | 5190 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell48data-Soc | BC48_SOC | 5191 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell49data-Voltage | BC49_U | 5192 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell49data-Current | BC49_I | 5193 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell49data-temperature | BC49_T | 5194 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell49data-Soc | BC49_SOC | 5195 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell50data-Voltage | BC50_U | 5196 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell50data-Current | BC50_I | 5197 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell50data-temperature | BC50_T | 5198 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell50data-Soc | BC50_SOC | 5199 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell51data-Voltage | BC51_U | 5200 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell51data-Current | BC51_I | 5201 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell51data-temperature | BC51_T | 5202 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell51data-Soc | BC51_SOC | 5203 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell52data-Voltage | BC52_U | 5204 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell52data-Current | BC52_I | 5205 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell52data-temperature | BC52_T | 5206 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell52data-Soc | BC52_SOC | 5207 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell53data-Voltage | BC53_U | 5208 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell53data-Current | BC53_I | 5209 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell53data-temperature | BC53_T | 5210 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell53data-Soc | BC53_SOC | 5211 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell54data-Voltage | BC54_U | 5212 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell54data-Current | BC54_I | 5213 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell54data-temperature | BC54_T | 5214 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell54data-Soc | BC54_SOC | 5215 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell55data-Voltage | BC55_U | 5216 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell55data-Current | BC55_I | 5217 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell55data-temperature | BC55_T | 5218 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell55data-Soc | BC55_SOC | 5219 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell56data-Voltage | BC56_U | 5220 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell56data-Current | BC56_I | 5221 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell56data-temperature | BC56_T | 5222 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell56data-Soc | BC56_SOC | 5223 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell57data-Voltage | BC57_U | 5224 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell57data-Current | BC57_I | 5225 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell57data-temperature | BC57_T | 5226 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell57data-Soc | BC57_SOC | 5227 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell58data-Voltage | BC58_U | 5228 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell58data-Current | BC58_I | 5229 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell58data-temperature | BC58_T | 5230 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell58data-Soc | BC58_SOC | 5231 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell59data-Voltage | BC59_U | 5232 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell59data-Current | BC59_I | 5233 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell59data-temperature | BC59_T | 5234 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell59data-Soc | BC59_SOC | 5235 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell60data-Voltage | BC60_U | 5236 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell60data-Current | BC60_I | 5237 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell60data-temperature | BC60_T | 5238 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell60data-Soc | BC60_SOC | 5239 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell61data-Voltage | BC61_U | 5240 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell61data-Current | BC61_I | 5241 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell61data-temperature | BC61_T | 5242 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell61data-Soc | BC61_SOC | 5243 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell62data-Voltage | BC62_U | 5244 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell62data-Current | BC62_I | 5245 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell62data-temperature | BC62_T | 5246 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell62data-Soc | BC62_SOC | 5247 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell63data-Voltage | BC63_U | 5248 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell63data-Current | BC63_I | 5249 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell63data-temperature | BC63_T | 5250 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell63data-Soc | BC63_SOC | 5251 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell64data-Voltage | BC64_U | 5252 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell64data-Current | BC64_I | 5253 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell64data-temperature | BC64_T | 5254 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell64data-Soc | BC64_SOC | 5255 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell65data-Voltage | BC65_U | 5256 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell65data-Current | BC65_I | 5257 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell65data-temperature | BC65_T | 5258 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell65data-Soc | BC65_SOC | 5259 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell66data-Voltage | BC66_U | 5260 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell66data-Current | BC66_I | 5261 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell66data-temperature | BC66_T | 5262 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell66data-Soc | BC66_SOC | 5263 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell67data-Voltage | BC67_U | 5264 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell67data-Current | BC67_I | 5265 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell67data-temperature | BC67_T | 5266 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell67data-Soc | BC67_SOC | 5267 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell68data-Voltage | BC68_U | 5268 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell68data-Current | BC68_I | 5269 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell68data-temperature | BC68_T | 5270 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell68data-Soc | BC68_SOC | 5271 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell69data-Voltage | BC69_U | 5272 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell69data-Current | BC69_I | 5273 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell69data-temperature | BC69_T | 5274 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell69data-Soc | BC69_SOC | 5275 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell70data-Voltage | BC70_U | 5276 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell70data-Current | BC70_I | 5277 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell70data-temperature | BC70_T | 5278 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell70data-Soc | BC70_SOC | 5279 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell71data-Voltage | BC71_U | 5280 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell71data-Current | BC71_I | 5281 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell71data-temperature | BC71_T | 5282 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell71data-Soc | BC71_SOC | 5283 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell72data-Voltage | BC72_U | 5284 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell72data-Current | BC72_I | 5285 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell72data-temperature | BC72_T | 5286 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell72data-Soc | BC72_SOC | 5287 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell73data-Voltage | BC73_U | 5288 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell73data-Current | BC73_I | 5289 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell73data-temperature | BC73_T | 5290 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell73data-Soc | BC73_SOC | 5291 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell74data-Voltage | BC74_U | 5292 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell74data-Current | BC74_I | 5293 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell74data-temperature | BC74_T | 5294 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell74data-Soc | BC74_SOC | 5295 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell75data-Voltage | BC75_U | 5296 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell75data-Current | BC75_I | 5297 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell75data-temperature | BC75_T | 5298 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell75data-Soc | BC75_SOC | 5299 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell76data-Voltage | BC76_U | 5300 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell76data-Current | BC76_I | 5301 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell76data-temperature | BC76_T | 5302 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell76data-Soc | BC76_SOC | 5303 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell77data-Voltage | BC77_U | 5304 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell77data-Current | BC77_I | 5305 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell77data-temperature | BC77_T | 5306 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell77data-Soc | BC77_SOC | 5307 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell78data-Voltage | BC78_U | 5308 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell78data-Current | BC78_I | 5309 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell78data-temperature | BC78_T | 5310 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell78data-Soc | BC78_SOC | 5311 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell79data-Voltage | BC79_U | 5312 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell79data-Current | BC79_I | 5313 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell79data-temperature | BC79_T | 5314 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell79data-Soc | BC79_SOC | 5315 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell80data-Voltage | BC80_U | 5316 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell80data-Current | BC80_I | 5317 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell80data-temperature | BC80_T | 5318 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell80data-Soc | BC80_SOC | 5319 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell81data-Voltage | BC81_U | 5320 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell81data-Current | BC81_I | 5321 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell81data-temperature | BC81_T | 5322 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell81data-Soc | BC81_SOC | 5323 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell82data-Voltage | BC82_U | 5324 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell82data-Current | BC82_I | 5325 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell82data-temperature | BC82_T | 5326 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell82data-Soc | BC82_SOC | 5327 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell83data-Voltage | BC83_U | 5328 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell83data-Current | BC83_I | 5329 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell83data-temperature | BC83_T | 5330 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell83data-Soc | BC83_SOC | 5331 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell84data-Voltage | BC84_U | 5332 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell84data-Current | BC84_I | 5333 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell84data-temperature | BC84_T | 5334 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell84data-Soc | BC84_SOC | 5335 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell85data-Voltage | BC85_U | 5336 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell85data-Current | BC85_I | 5337 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell85data-temperature | BC85_T | 5338 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell85data-Soc | BC85_SOC | 5339 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell86data-Voltage | BC86_U | 5340 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell86data-Current | BC86_I | 5341 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell86data-temperature | BC86_T | 5342 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell86data-Soc | BC86_SOC | 5343 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell87data-Voltage | BC87_U | 5344 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell87data-Current | BC87_I | 5345 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell87data-temperature | BC87_T | 5346 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell87data-Soc | BC87_SOC | 5347 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell88data-Voltage | BC88_U | 5348 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell88data-Current | BC88_I | 5349 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell88data-temperature | BC88_T | 5350 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell88data-Soc | BC88_SOC | 5351 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell89data-Voltage | BC89_U | 5352 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell89data-Current | BC89_I | 5353 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell89data-temperature | BC89_T | 5354 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell89data-Soc | BC89_SOC | 5355 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell90data-Voltage | BC90_U | 5356 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell90data-Current | BC90_I | 5357 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell90data-temperature | BC90_T | 5358 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell90data-Soc | BC90_SOC | 5359 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell91data-Voltage | BC91_U | 5360 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell91data-Current | BC91_I | 5361 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell91data-temperature | BC91_T | 5362 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell91data-Soc | BC91_SOC | 5363 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell92data-Voltage | BC92_U | 5364 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell92data-Current | BC92_I | 5365 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell92data-temperature | BC92_T | 5366 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell92data-Soc | BC92_SOC | 5367 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell93data-Voltage | BC93_U | 5368 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell93data-Current | BC93_I | 5369 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell93data-temperature | BC93_T | 5370 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell93data-Soc | BC93_SOC | 5371 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell94data-Voltage | BC94_U | 5372 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell94data-Current | BC94_I | 5373 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell94data-temperature | BC94_T | 5374 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell94data-Soc | BC94_SOC | 5375 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell95data-Voltage | BC95_U | 5376 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell95data-Current | BC95_I | 5377 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell95data-temperature | BC95_T | 5378 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell95data-Soc | BC95_SOC | 5379 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell96data-Voltage | BC96_U | 5380 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell96data-Current | BC96_I | 5381 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell96data-temperature | BC96_T | 5382 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell96data-Soc | BC96_SOC | 5383 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell97data-Voltage | BC97_U | 5384 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell97data-Current | BC97_I | 5385 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell97data-temperature | BC97_T | 5386 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell97data-Soc | BC97_SOC | 5387 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell98data-Voltage | BC98_U | 5388 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell98data-Current | BC98_I | 5389 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell98data-temperature | BC98_T | 5390 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell98data-Soc | BC98_SOC | 5391 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell99data-Voltage | BC99_U | 5392 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell99data-Current | BC99_I | 5393 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell99data-temperature | BC99_T | 5394 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell99data-Soc | BC99_SOC | 5395 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell100data-Voltage | BC100_U | 5396 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell100data-Current | BC100_I | 5397 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell100data-temperature | BC100_T | 5398 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell100data-Soc | BC100_SOC | 5399 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell101data-Voltage | BC101_U | 5400 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell101data-Current | BC101_I | 5401 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell101data-temperature | BC101_T | 5402 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell101data-Soc | BC101_SOC | 5403 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell102data-Voltage | BC102_U | 5404 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell102data-Current | BC102_I | 5405 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell102data-temperature | BC102_T | 5406 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell102data-Soc | BC102_SOC | 5407 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell103data-Voltage | BC103_U | 5408 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell103data-Current | BC103_I | 5409 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell103data-temperature | BC103_T | 5410 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell103data-Soc | BC103_SOC | 5411 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell104data-Voltage | BC104_U | 5412 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell104data-Current | BC104_I | 5413 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell104data-temperature | BC104_T | 5414 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell104data-Soc | BC104_SOC | 5415 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell105data-Voltage | BC105_U | 5416 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell105data-Current | BC105_I | 5417 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell105data-temperature | BC105_T | 5418 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell105data-Soc | BC105_SOC | 5419 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell106data-Voltage | BC106_U | 5420 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell106data-Current | BC106_I | 5421 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell106data-temperature | BC106_T | 5422 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell106data-Soc | BC106_SOC | 5423 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell107data-Voltage | BC107_U | 5424 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell107data-Current | BC107_I | 5425 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell107data-temperature | BC107_T | 5426 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell107data-Soc | BC107_SOC | 5427 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell108data-Voltage | BC108_U | 5428 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell108data-Current | BC108_I | 5429 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell108data-temperature | BC108_T | 5430 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell108data-Soc | BC108_SOC | 5431 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell109data-Voltage | BC109_U | 5432 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell109data-Current | BC109_I | 5433 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell109data-temperature | BC109_T | 5434 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell109data-Soc | BC109_SOC | 5435 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell110data-Voltage | BC110_U | 5436 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell110data-Current | BC110_I | 5437 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell110data-temperature | BC110_T | 5438 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell110data-Soc | BC110_SOC | 5439 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell111data-Voltage | BC111_U | 5440 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell111data-Current | BC111_I | 5441 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell111data-temperature | BC111_T | 5442 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell111data-Soc | BC111_SOC | 5443 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell112data-Voltage | BC112_U | 5444 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell112data-Current | BC112_I | 5445 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell112data-temperature | BC112_T | 5446 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell112data-Soc | BC112_SOC | 5447 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell113data-Voltage | BC113_U | 5448 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell113data-Current | BC113_I | 5449 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell113data-temperature | BC113_T | 5450 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell113data-Soc | BC113_SOC | 5451 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell114data-Voltage | BC114_U | 5452 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell114data-Current | BC114_I | 5453 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell114data-temperature | BC114_T | 5454 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell114data-Soc | BC114_SOC | 5455 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell115data-Voltage | BC115_U | 5456 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell115data-Current | BC115_I | 5457 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell115data-temperature | BC115_T | 5458 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell115data-Soc | BC115_SOC | 5459 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell116data-Voltage | BC116_U | 5460 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell116data-Current | BC116_I | 5461 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell116data-temperature | BC116_T | 5462 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell116data-Soc | BC116_SOC | 5463 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell117data-Voltage | BC117_U | 5464 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell117data-Current | BC117_I | 5465 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell117data-temperature | BC117_T | 5466 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell117data-Soc | BC117_SOC | 5467 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell118data-Voltage | BC118_U | 5468 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell118data-Current | BC118_I | 5469 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell118data-temperature | BC118_T | 5470 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell118data-Soc | BC118_SOC | 5471 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell119data-Voltage | BC119_U | 5472 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell119data-Current | BC119_I | 5473 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell119data-temperature | BC119_T | 5474 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell119data-Soc | BC119_SOC | 5475 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell120data-Voltage | BC120_U | 5476 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell120data-Current | BC120_I | 5477 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell120data-temperature | BC120_T | 5478 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell120data-Soc | BC120_SOC | 5479 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell121data-Voltage | BC121_U | 5480 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell121data-Current | BC121_I | 5481 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell121data-temperature | BC121_T | 5482 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell121data-Soc | BC121_SOC | 5483 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell122data-Voltage | BC122_U | 5484 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell122data-Current | BC122_I | 5485 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell122data-temperature | BC122_T | 5486 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell122data-Soc | BC122_SOC | 5487 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell123data-Voltage | BC123_U | 5488 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell123data-Current | BC123_I | 5489 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell123data-temperature | BC123_T | 5490 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell123data-Soc | BC123_SOC | 5491 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell124data-Voltage | BC124_U | 5492 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell124data-Current | BC124_I | 5493 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell124data-temperature | BC124_T | 5494 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell124data-Soc | BC124_SOC | 5495 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell125data-Voltage | BC125_U | 5496 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell125data-Current | BC125_I | 5497 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell125data-temperature | BC125_T | 5498 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell125data-Soc | BC125_SOC | 5499 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell126data-Voltage | BC126_U | 5500 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell126data-Current | BC126_I | 5501 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell126data-temperature | BC126_T | 5502 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell126data-Soc | BC126_SOC | 5503 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell127data-Voltage | BC127_U | 5504 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell127data-Current | BC127_I | 5505 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell127data-temperature | BC127_T | 5506 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell127data-Soc | BC127_SOC | 5507 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell128data-Voltage | BC128_U | 5508 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell128data-Current | BC128_I | 5509 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell128data-temperature | BC128_T | 5510 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell128data-Soc | BC128_SOC | 5511 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell129data-Voltage | BC129_U | 5512 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell129data-Current | BC129_I | 5513 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell129data-temperature | BC129_T | 5514 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell129data-Soc | BC129_SOC | 5515 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell130data-Voltage | BC130_U | 5516 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell130data-Current | BC130_I | 5517 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell130data-temperature | BC130_T | 5518 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell130data-Soc | BC130_SOC | 5519 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell131data-Voltage | BC131_U | 5520 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell131data-Current | BC131_I | 5521 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell131data-temperature | BC131_T | 5522 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell131data-Soc | BC131_SOC | 5523 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell132data-Voltage | BC132_U | 5524 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell132data-Current | BC132_I | 5525 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell132data-temperature | BC132_T | 5526 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell132data-Soc | BC132_SOC | 5527 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell133data-Voltage | BC133_U | 5528 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell133data-Current | BC133_I | 5529 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell133data-temperature | BC133_T | 5530 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell133data-Soc | BC133_SOC | 5531 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell134data-Voltage | BC134_U | 5532 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell134data-Current | BC134_I | 5533 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell134data-temperature | BC134_T | 5534 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell134data-Soc | BC134_SOC | 5535 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell135data-Voltage | BC135_U | 5536 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell135data-Current | BC135_I | 5537 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell135data-temperature | BC135_T | 5538 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell135data-Soc | BC135_SOC | 5539 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell136data-Voltage | BC136_U | 5540 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell136data-Current | BC136_I | 5541 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell136data-temperature | BC136_T | 5542 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell136data-Soc | BC136_SOC | 5543 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell137data-Voltage | BC137_U | 5544 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell137data-Current | BC137_I | 5545 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell137data-temperature | BC137_T | 5546 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell137data-Soc | BC137_SOC | 5547 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell138data-Voltage | BC138_U | 5548 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell138data-Current | BC138_I | 5549 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell138data-temperature | BC138_T | 5550 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell138data-Soc | BC138_SOC | 5551 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell139data-Voltage | BC139_U | 5552 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell139data-Current | BC139_I | 5553 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell139data-temperature | BC139_T | 5554 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell139data-Soc | BC139_SOC | 5555 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell140data-Voltage | BC140_U | 5556 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell140data-Current | BC140_I | 5557 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell140data-temperature | BC140_T | 5558 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell140data-Soc | BC140_SOC | 5559 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell141data-Voltage | BC141_U | 5560 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell141data-Current | BC141_I | 5561 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell141data-temperature | BC141_T | 5562 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell141data-Soc | BC141_SOC | 5563 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell142data-Voltage | BC142_U | 5564 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell142data-Current | BC142_I | 5565 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell142data-temperature | BC142_T | 5566 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell142data-Soc | BC142_SOC | 5567 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell143data-Voltage | BC143_U | 5568 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell143data-Current | BC143_I | 5569 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell143data-temperature | BC143_T | 5570 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell143data-Soc | BC143_SOC | 5571 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell144data-Voltage | BC144_U | 5572 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell144data-Current | BC144_I | 5573 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell144data-temperature | BC144_T | 5574 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell144data-Soc | BC144_SOC | 5575 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell145data-Voltage | BC145_U | 5576 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell145data-Current | BC145_I | 5577 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell145data-temperature | BC145_T | 5578 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell145data-Soc | BC145_SOC | 5579 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell146data-Voltage | BC146_U | 5580 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell146data-Current | BC146_I | 5581 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell146data-temperature | BC146_T | 5582 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell146data-Soc | BC146_SOC | 5583 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell147data-Voltage | BC147_U | 5584 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell147data-Current | BC147_I | 5585 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell147data-temperature | BC147_T | 5586 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell147data-Soc | BC147_SOC | 5587 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell148data-Voltage | BC148_U | 5588 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell148data-Current | BC148_I | 5589 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell148data-temperature | BC148_T | 5590 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell148data-Soc | BC148_SOC | 5591 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell149data-Voltage | BC149_U | 5592 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell149data-Current | BC149_I | 5593 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell149data-temperature | BC149_T | 5594 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell149data-Soc | BC149_SOC | 5595 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell150data-Voltage | BC150_U | 5596 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell150data-Current | BC150_I | 5597 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell150data-temperature | BC150_T | 5598 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell150data-Soc | BC150_SOC | 5599 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell151data-Voltage | BC151_U | 5600 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell151data-Current | BC151_I | 5601 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell151data-temperature | BC151_T | 5602 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell151data-Soc | BC151_SOC | 5603 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell152data-Voltage | BC152_U | 5604 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell152data-Current | BC152_I | 5605 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell152data-temperature | BC152_T | 5606 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell152data-Soc | BC152_SOC | 5607 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell153data-Voltage | BC153_U | 5608 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell153data-Current | BC153_I | 5609 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell153data-temperature | BC153_T | 5610 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell153data-Soc | BC153_SOC | 5611 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell154data-Voltage | BC154_U | 5612 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell154data-Current | BC154_I | 5613 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell154data-temperature | BC154_T | 5614 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell154data-Soc | BC154_SOC | 5615 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell155data-Voltage | BC155_U | 5616 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell155data-Current | BC155_I | 5617 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell155data-temperature | BC155_T | 5618 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell155data-Soc | BC155_SOC | 5619 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell156data-Voltage | BC156_U | 5620 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell156data-Current | BC156_I | 5621 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell156data-temperature | BC156_T | 5622 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell156data-Soc | BC156_SOC | 5623 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell157data-Voltage | BC157_U | 5624 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell157data-Current | BC157_I | 5625 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell157data-temperature | BC157_T | 5626 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell157data-Soc | BC157_SOC | 5627 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell158data-Voltage | BC158_U | 5628 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell158data-Current | BC158_I | 5629 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell158data-temperature | BC158_T | 5630 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell158data-Soc | BC158_SOC | 5631 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell159data-Voltage | BC159_U | 5632 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell159data-Current | BC159_I | 5633 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell159data-temperature | BC159_T | 5634 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell159data-Soc | BC159_SOC | 5635 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell160data-Voltage | BC160_U | 5636 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell160data-Current | BC160_I | 5637 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell160data-temperature | BC160_T | 5638 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell160data-Soc | BC160_SOC | 5639 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell161data-Voltage | BC161_U | 5640 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell161data-Current | BC161_I | 5641 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell161data-temperature | BC161_T | 5642 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell161data-Soc | BC161_SOC | 5643 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell162data-Voltage | BC162_U | 5644 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell162data-Current | BC162_I | 5645 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell162data-temperature | BC162_T | 5646 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell162data-Soc | BC162_SOC | 5647 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell163data-Voltage | BC163_U | 5648 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell163data-Current | BC163_I | 5649 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell163data-temperature | BC163_T | 5650 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell163data-Soc | BC163_SOC | 5651 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell164data-Voltage | BC164_U | 5652 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell164data-Current | BC164_I | 5653 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell164data-temperature | BC164_T | 5654 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell164data-Soc | BC164_SOC | 5655 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell165data-Voltage | BC165_U | 5656 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell165data-Current | BC165_I | 5657 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell165data-temperature | BC165_T | 5658 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell165data-Soc | BC165_SOC | 5659 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell166data-Voltage | BC166_U | 5660 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell166data-Current | BC166_I | 5661 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell166data-temperature | BC166_T | 5662 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell166data-Soc | BC166_SOC | 5663 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell167data-Voltage | BC167_U | 5664 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell167data-Current | BC167_I | 5665 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell167data-temperature | BC167_T | 5666 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell167data-Soc | BC167_SOC | 5667 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell168data-Voltage | BC168_U | 5668 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell168data-Current | BC168_I | 5669 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell168data-temperature | BC168_T | 5670 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell168data-Soc | BC168_SOC | 5671 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell169data-Voltage | BC169_U | 5672 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell169data-Current | BC169_I | 5673 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell169data-temperature | BC169_T | 5674 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell169data-Soc | BC169_SOC | 5675 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell170data-Voltage | BC170_U | 5676 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell170data-Current | BC170_I | 5677 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell170data-temperature | BC170_T | 5678 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell170data-Soc | BC170_SOC | 5679 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell171data-Voltage | BC171_U | 5680 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell171data-Current | BC171_I | 5681 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell171data-temperature | BC171_T | 5682 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell171data-Soc | BC171_SOC | 5683 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell172data-Voltage | BC172_U | 5684 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell172data-Current | BC172_I | 5685 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell172data-temperature | BC172_T | 5686 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell172data-Soc | BC172_SOC | 5687 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell173data-Voltage | BC173_U | 5688 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell173data-Current | BC173_I | 5689 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell173data-temperature | BC173_T | 5690 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell173data-Soc | BC173_SOC | 5691 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell174data-Voltage | BC174_U | 5692 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell174data-Current | BC174_I | 5693 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell174data-temperature | BC174_T | 5694 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell174data-Soc | BC174_SOC | 5695 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell175data-Voltage | BC175_U | 5696 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell175data-Current | BC175_I | 5697 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell175data-temperature | BC175_T | 5698 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell175data-Soc | BC175_SOC | 5699 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell176data-Voltage | BC176_U | 5700 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell176data-Current | BC176_I | 5701 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell176data-temperature | BC176_T | 5702 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell176data-Soc | BC176_SOC | 5703 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell177data-Voltage | BC177_U | 5704 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell177data-Current | BC177_I | 5705 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell177data-temperature | BC177_T | 5706 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell177data-Soc | BC177_SOC | 5707 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell178data-Voltage | BC178_U | 5708 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell178data-Current | BC178_I | 5709 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell178data-temperature | BC178_T | 5710 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell178data-Soc | BC178_SOC | 5711 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell179data-Voltage | BC179_U | 5712 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell179data-Current | BC179_I | 5713 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell179data-temperature | BC179_T | 5714 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell179data-Soc | BC179_SOC | 5715 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell180data-Voltage | BC180_U | 5716 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell180data-Current | BC180_I | 5717 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell180data-temperature | BC180_T | 5718 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell180data-Soc | BC180_SOC | 5719 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell181data-Voltage | BC181_U | 5720 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell181data-Current | BC181_I | 5721 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell181data-temperature | BC181_T | 5722 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell181data-Soc | BC181_SOC | 5723 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell182data-Voltage | BC182_U | 5724 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell182data-Current | BC182_I | 5725 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell182data-temperature | BC182_T | 5726 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell182data-Soc | BC182_SOC | 5727 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell183data-Voltage | BC183_U | 5728 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell183data-Current | BC183_I | 5729 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell183data-temperature | BC183_T | 5730 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell183data-Soc | BC183_SOC | 5731 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell184data-Voltage | BC184_U | 5732 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell184data-Current | BC184_I | 5733 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell184data-temperature | BC184_T | 5734 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell184data-Soc | BC184_SOC | 5735 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell185data-Voltage | BC185_U | 5736 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell185data-Current | BC185_I | 5737 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell185data-temperature | BC185_T | 5738 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell185data-Soc | BC185_SOC | 5739 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell186data-Voltage | BC186_U | 5740 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell186data-Current | BC186_I | 5741 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell186data-temperature | BC186_T | 5742 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell186data-Soc | BC186_SOC | 5743 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell187data-Voltage | BC187_U | 5744 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell187data-Current | BC187_I | 5745 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell187data-temperature | BC187_T | 5746 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell187data-Soc | BC187_SOC | 5747 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell188data-Voltage | BC188_U | 5748 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell188data-Current | BC188_I | 5749 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell188data-temperature | BC188_T | 5750 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell188data-Soc | BC188_SOC | 5751 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell189data-Voltage | BC189_U | 5752 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell189data-Current | BC189_I | 5753 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell189data-temperature | BC189_T | 5754 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell189data-Soc | BC189_SOC | 5755 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell190data-Voltage | BC190_U | 5756 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell190data-Current | BC190_I | 5757 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell190data-temperature | BC190_T | 5758 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell190data-Soc | BC190_SOC | 5759 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell191data-Voltage | BC191_U | 5760 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell191data-Current | BC191_I | 5761 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell191data-temperature | BC191_T | 5762 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell191data-Soc | BC191_SOC | 5763 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell192data-Voltage | BC192_U | 5764 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell192data-Current | BC192_I | 5765 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell192data-temperature | BC192_T | 5766 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell192data-Soc | BC192_SOC | 5767 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell193data-Voltage | BC193_U | 5768 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell193data-Current | BC193_I | 5769 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell193data-temperature | BC193_T | 5770 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell193data-Soc | BC193_SOC | 5771 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell194data-Voltage | BC194_U | 5772 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell194data-Current | BC194_I | 5773 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell194data-temperature | BC194_T | 5774 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell194data-Soc | BC194_SOC | 5775 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell195data-Voltage | BC195_U | 5776 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell195data-Current | BC195_I | 5777 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell195data-temperature | BC195_T | 5778 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell195data-Soc | BC195_SOC | 5779 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell196data-Voltage | BC196_U | 5780 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell196data-Current | BC196_I | 5781 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell196data-temperature | BC196_T | 5782 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell196data-Soc | BC196_SOC | 5783 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell197data-Voltage | BC197_U | 5784 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell197data-Current | BC197_I | 5785 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell197data-temperature | BC197_T | 5786 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell197data-Soc | BC197_SOC | 5787 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell198data-Voltage | BC198_U | 5788 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell198data-Current | BC198_I | 5789 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell198data-temperature | BC198_T | 5790 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell198data-Soc | BC198_SOC | 5791 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell199data-Voltage | BC199_U | 5792 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell199data-Current | BC199_I | 5793 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell199data-temperature | BC199_T | 5794 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell199data-Soc | BC199_SOC | 5795 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell200data-Voltage | BC200_U | 5796 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell200data-Current | BC200_I | 5797 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell200data-temperature | BC200_T | 5798 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell200data-Soc | BC200_SOC | 5799 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell201data-Voltage | BC201_U | 5800 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell201data-Current | BC201_I | 5801 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell201data-temperature | BC201_T | 5802 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell201data-Soc | BC201_SOC | 5803 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell202data-Voltage | BC202_U | 5804 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell202data-Current | BC202_I | 5805 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell202data-temperature | BC202_T | 5806 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell202data-Soc | BC202_SOC | 5807 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell203data-Voltage | BC203_U | 5808 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell203data-Current | BC203_I | 5809 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell203data-temperature | BC203_T | 5810 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell203data-Soc | BC203_SOC | 5811 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell204data-Voltage | BC204_U | 5812 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell204data-Current | BC204_I | 5813 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell204data-temperature | BC204_T | 5814 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell204data-Soc | BC204_SOC | 5815 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell205data-Voltage | BC205_U | 5816 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell205data-Current | BC205_I | 5817 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell205data-temperature | BC205_T | 5818 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell205data-Soc | BC205_SOC | 5819 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell206data-Voltage | BC206_U | 5820 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell206data-Current | BC206_I | 5821 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell206data-temperature | BC206_T | 5822 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell206data-Soc | BC206_SOC | 5823 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell207data-Voltage | BC207_U | 5824 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell207data-Current | BC207_I | 5825 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell207data-temperature | BC207_T | 5826 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell207data-Soc | BC207_SOC | 5827 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell208data-Voltage | BC208_U | 5828 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell208data-Current | BC208_I | 5829 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell208data-temperature | BC208_T | 5830 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell208data-Soc | BC208_SOC | 5831 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell209data-Voltage | BC209_U | 5832 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell209data-Current | BC209_I | 5833 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell209data-temperature | BC209_T | 5834 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell209data-Soc | BC209_SOC | 5835 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell210data-Voltage | BC210_U | 5836 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell210data-Current | BC210_I | 5837 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell210data-temperature | BC210_T | 5838 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell210data-Soc | BC210_SOC | 5839 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell211data-Voltage | BC211_U | 5840 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell211data-Current | BC211_I | 5841 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell211data-temperature | BC211_T | 5842 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell211data-Soc | BC211_SOC | 5843 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell212data-Voltage | BC212_U | 5844 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell212data-Current | BC212_I | 5845 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell212data-temperature | BC212_T | 5846 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell212data-Soc | BC212_SOC | 5847 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell213data-Voltage | BC213_U | 5848 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell213data-Current | BC213_I | 5849 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell213data-temperature | BC213_T | 5850 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell213data-Soc | BC213_SOC | 5851 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell214data-Voltage | BC214_U | 5852 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell214data-Current | BC214_I | 5853 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell214data-temperature | BC214_T | 5854 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell214data-Soc | BC214_SOC | 5855 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell215data-Voltage | BC215_U | 5856 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell215data-Current | BC215_I | 5857 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell215data-temperature | BC215_T | 5858 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell215data-Soc | BC215_SOC | 5859 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell216data-Voltage | BC216_U | 5860 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell216data-Current | BC216_I | 5861 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell216data-temperature | BC216_T | 5862 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell216data-Soc | BC216_SOC | 5863 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell217data-Voltage | BC217_U | 5864 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell217data-Current | BC217_I | 5865 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell217data-temperature | BC217_T | 5866 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell217data-Soc | BC217_SOC | 5867 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell218data-Voltage | BC218_U | 5868 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell218data-Current | BC218_I | 5869 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell218data-temperature | BC218_T | 5870 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell218data-Soc | BC218_SOC | 5871 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell219data-Voltage | BC219_U | 5872 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell219data-Current | BC219_I | 5873 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell219data-temperature | BC219_T | 5874 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell219data-Soc | BC219_SOC | 5875 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell220data-Voltage | BC220_U | 5876 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell220data-Current | BC220_I | 5877 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell220data-temperature | BC220_T | 5878 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell220data-Soc | BC220_SOC | 5879 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell221data-Voltage | BC221_U | 5880 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell221data-Current | BC221_I | 5881 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell221data-temperature | BC221_T | 5882 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell221data-Soc | BC221_SOC | 5883 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell222data-Voltage | BC222_U | 5884 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell222data-Current | BC222_I | 5885 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell222data-temperature | BC222_T | 5886 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell222data-Soc | BC222_SOC | 5887 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell223data-Voltage | BC223_U | 5888 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell223data-Current | BC223_I | 5889 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell223data-temperature | BC223_T | 5890 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell223data-Soc | BC223_SOC | 5891 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell224data-Voltage | BC224_U | 5892 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell224data-Current | BC224_I | 5893 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell224data-temperature | BC224_T | 5894 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell224data-Soc | BC224_SOC | 5895 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell225data-Voltage | BC225_U | 5896 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell225data-Current | BC225_I | 5897 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell225data-temperature | BC225_T | 5898 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell225data-Soc | BC225_SOC | 5899 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell226data-Voltage | BC226_U | 5900 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell226data-Current | BC226_I | 5901 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell226data-temperature | BC226_T | 5902 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell226data-Soc | BC226_SOC | 5903 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell227data-Voltage | BC227_U | 5904 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell227data-Current | BC227_I | 5905 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell227data-temperature | BC227_T | 5906 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell227data-Soc | BC227_SOC | 5907 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell228data-Voltage | BC228_U | 5908 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell228data-Current | BC228_I | 5909 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell228data-temperature | BC228_T | 5910 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell228data-Soc | BC228_SOC | 5911 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell229data-Voltage | BC229_U | 5912 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell229data-Current | BC229_I | 5913 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell229data-temperature | BC229_T | 5914 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell229data-Soc | BC229_SOC | 5915 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell230data-Voltage | BC230_U | 5916 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell230data-Current | BC230_I | 5917 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell230data-temperature | BC230_T | 5918 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell230data-Soc | BC230_SOC | 5919 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell231data-Voltage | BC231_U | 5920 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell231data-Current | BC231_I | 5921 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell231data-temperature | BC231_T | 5922 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell231data-Soc | BC231_SOC | 5923 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell232data-Voltage | BC232_U | 5924 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell232data-Current | BC232_I | 5925 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell232data-temperature | BC232_T | 5926 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell232data-Soc | BC232_SOC | 5927 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell233data-Voltage | BC233_U | 5928 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell233data-Current | BC233_I | 5929 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell233data-temperature | BC233_T | 5930 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell233data-Soc | BC233_SOC | 5931 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell234data-Voltage | BC234_U | 5932 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell234data-Current | BC234_I | 5933 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell234data-temperature | BC234_T | 5934 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell234data-Soc | BC234_SOC | 5935 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell235data-Voltage | BC235_U | 5936 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell235data-Current | BC235_I | 5937 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell235data-temperature | BC235_T | 5938 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell235data-Soc | BC235_SOC | 5939 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell236data-Voltage | BC236_U | 5940 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell236data-Current | BC236_I | 5941 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell236data-temperature | BC236_T | 5942 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell236data-Soc | BC236_SOC | 5943 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell237data-Voltage | BC237_U | 5944 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell237data-Current | BC237_I | 5945 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell237data-temperature | BC237_T | 5946 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell237data-Soc | BC237_SOC | 5947 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell238data-Voltage | BC238_U | 5948 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell238data-Current | BC238_I | 5949 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell238data-temperature | BC238_T | 5950 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell238data-Soc | BC238_SOC | 5951 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell239data-Voltage | BC239_U | 5952 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell239data-Current | BC239_I | 5953 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell239data-temperature | BC239_T | 5954 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell239data-Soc | BC239_SOC | 5955 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell240data-Voltage | BC240_U | 5956 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell240data-Current | BC240_I | 5957 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell240data-temperature | BC240_T | 5958 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell240data-Soc | BC240_SOC | 5959 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell241data-Voltage | BC241_U | 5960 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell241data-Current | BC241_I | 5961 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell241data-temperature | BC241_T | 5962 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell241data-Soc | BC241_SOC | 5963 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell242data-Voltage | BC242_U | 5964 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell242data-Current | BC242_I | 5965 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell242data-temperature | BC242_T | 5966 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell242data-Soc | BC242_SOC | 5967 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell243data-Voltage | BC243_U | 5968 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell243data-Current | BC243_I | 5969 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell243data-temperature | BC243_T | 5970 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell243data-Soc | BC243_SOC | 5971 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell244data-Voltage | BC244_U | 5972 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell244data-Current | BC244_I | 5973 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell244data-temperature | BC244_T | 5974 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell244data-Soc | BC244_SOC | 5975 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell245data-Voltage | BC245_U | 5976 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell245data-Current | BC245_I | 5977 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell245data-temperature | BC245_T | 5978 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell245data-Soc | BC245_SOC | 5979 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell246data-Voltage | BC246_U | 5980 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell246data-Current | BC246_I | 5981 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell246data-temperature | BC246_T | 5982 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell246data-Soc | BC246_SOC | 5983 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell247data-Voltage | BC247_U | 5984 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell247data-Current | BC247_I | 5985 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell247data-temperature | BC247_T | 5986 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell247data-Soc | BC247_SOC | 5987 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell248data-Voltage | BC248_U | 5988 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell248data-Current | BC248_I | 5989 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell248data-temperature | BC248_T | 5990 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell248data-Soc | BC248_SOC | 5991 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell249data-Voltage | BC249_U | 5992 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell249data-Current | BC249_I | 5993 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell249data-temperature | BC249_T | 5994 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell249data-Soc | BC249_SOC | 5995 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell250data-Voltage | BC250_U | 5996 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell250data-Current | BC250_I | 5997 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell250data-temperature | BC250_T | 5998 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell250data-Soc | BC250_SOC | 5999 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell251data-Voltage | BC251_U | 6000 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell251data-Current | BC251_I | 6001 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell251data-temperature | BC251_T | 6002 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell251data-Soc | BC251_SOC | 6003 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell252data-Voltage | BC252_U | 6004 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell252data-Current | BC252_I | 6005 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell252data-temperature | BC252_T | 6006 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell252data-Soc | BC252_SOC | 6007 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell253data-Voltage | BC253_U | 6008 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell253data-Current | BC253_I | 6009 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell253data-temperature | BC253_T | 6010 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell253data-Soc | BC253_SOC | 6011 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell254data-Voltage | BC254_U | 6012 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell254data-Current | BC254_I | 6013 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell254data-temperature | BC254_T | 6014 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell254data-Soc | BC254_SOC | 6015 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell255data-Voltage | BC255_U | 6016 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell255data-Current | BC255_I | 6017 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell255data-temperature | BC255_T | 6018 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell255data-Soc | BC255_SOC | 6019 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X
√ | cell256data-Voltage | BC256_U | 6020 | S16 | 2 |  | mV |  |  |  | X | √ | X | X
√ | cell256data-Current | BC256_I | 6021 | S16 | 2 |  | 0.01A |  |  |  | X | √ | X | X
√ | cell256data-temperature | BC256_T | 6022 | S16 | 2 |  | 0.1℃ |  |  |  | X | √ | X | X
√ | cell256data-Soc | BC256_SOC | 6023 | S16 | 2 |  | 1% |  |  |  | X | √ | X | X

## Parameter Reading and Writing 0
Hybrid Inverter | Name | Name-abridge | Address | Type Of Data | Number of bytes | Data Range | Unit | Remark | Whether to store externally Flash | modification | variable name | 0x03 | 0x04 | 0x06 | 0x10
| Setting Parameter 1 (system parameters) | [10 empty] | function code
√ | Safety selection | Safty | 204 | U16 | 2 | Safty |  | After setting, you need to restart the inverter. | YES |  | guwDeSafty | √ | X | √ | √
√ | PV input mode | PVInputType | 205 | U16 | 2 | 0:Independent 1:Parallel 2:NoPv |  | Default: 0: independent | YES | Add 2: No PV | guwDePvInputType | √ | X | √ | √
√ | Run function enable | FuncEn | 206-207 | U32 | 4 | Run function enable |  |  | YES |  | gulDeSysFuncEn | √ | X | √ | √
√ | Protection function enabled | ProtectEn | 208-209 | U32 | 4 | Protection function enabled |  |  | YES |  | gulDeSysProtectEn | √ | X | √ | √
√ | PV starting voltage | PvStartVolt | 210 | U16 | 2 | 800-10000 | 0.1V |  | YES |  | guwDeStartVpv | √ | X | √ | √
√ | CT or Meter | MeterType | 211 | U16 | 2 | 0：no merter 1：CT 2：meter 3.Dual-CT 4.Dual-meter 5.CT-Merter 6.Merter-CT |  | default：1：CT | YES |  | guwDeMeterType | √ | X | √ | √
√ | MeterBrand | MeterBrand | 212 | U16 | 2 | 0：Afore 1：Afore3 2: UKOB418 3: UKOB115 4: ADL200 5: ADL400 6:Livoltek-3p 7:Chint-3p |  | default：1：Afore3 | YES | 21.8.30 Extend data range | guwDeMeterBrand | √ | X | √ | √
√ | CTRatio | CTRatio | 213 | U16 | 2 | 0-100 |  | default：100 | YES |  |  | √ | X | √ | √
√ | ParallOperateOnOff | ParallOperateOnOff | 236 | U16 |  |  |  | 170：Stop inverter paralleling 187：Enable inverter paralleling | YES |  |  | √ | X | √ | √
√ | Parallel number and serial number settings | InverterSumAndID | 237 | U16 |  | InverterSum：2-6 InverterID：0-5 |  | B0-B7: InverterSum B8-B15: InverterID(0：Master，1：Slave1,2：Slave2，3：Slave3，4：Slave4，5：Slave5) | YES |  |  | √ | X | √ | √
√ | Reserve | Reserve | 238-499 | [8 empty] | √ | X | √ | √
| Setting Parameter 2 (system command) | [10 empty] | √ | X | √ | √
√ | Function execution instructions | FuncCmd | 527-528 | U32 | 4 | B3: forced reset B4: restore factory B5: clear records |  | B3: Forced reset B4: Restore Factory B5: Clear record information |  |  | gulDeSysFuncCmd | √ | X | √ | √
| Setting Parameter 3 (Protection Parameter) | [10 empty] | √ | X | √ | √
√ | Grid connection condition judgment time | GridOnJudgTime | 1000 | U16 | 2 | 10-1200 | S |  | YES |  | guwDeGridOnJudgT | √ | X | √ | √
√ | Maximum voltage allowed for grid connection | GridOnVoltMax | 1001 | U16 | 2 | 1010-3200 | 0.1V |  | YES |  | guwDeGridOnVMax | √ | X | √ | √
√ | Minimum voltage allowed for grid connection | GridOnVoltMin | 1002 | U16 | 2 | 500-2300 | 0.1V |  | YES |  | guwDeGridOnVMin | √ | X | √ | √
√ | Maximum frequency allowed for grid connection | GridOnFreqMax | 1003 | U16 | 2 | 5000-7000 | 0.01Hz |  | YES |  | guwDeGridOnFMax | √ | X | √ | √
√ | Minimum frequency allowed for grid connection | GridOnFreqMin | 1004 | U16 | 2 | 4000-6000 | 0.01Hz |  | YES | 21.8.30 Add new unit | guwDeGridOnFMin | √ | X | √ | √
√ | Voltage protection level trip selection | VoltProtectStage | 1005 | U16 | 2 | 1-5 |  | 1: Level 1 default Level 1 2: Level 2 3: Level 3 4: Level 4 5: Level 5 | YES |  | guwDeVoltProtectStage | √ | X | √ | √
√ | Frequency protection level trip selection | FreqProtectStage | 1006 | U16 | 2 | 1-5 |  | 1: Level 1 default Level 1 2: Level 2 3: Level 3 4: Level 4 5: Level 5 | YES |  | guwDeFreqProtectStage | √ | X | √ | √
√ | Grid overvoltage recovery point | GridVoltMaxRecover | 1007 | U16 | 2 | 1010-3200 | 0.1V |  | YES |  | guwDeGridVMaxRec | √ | X | √ | √
√ | Grid undervoltage recovery point | GridVoltMinRecover | 1008 | U16 | 2 | 500-2300 | 0.1V |  | YES |  | guwDeGridVMinRec | √ | X | √ | √
√ | Grid overfrequency recovery point | GridFreqMaxRecover | 1009 | U16 | 2 | 5000-7000 | 0.01Hz |  | YES |  | guwDeGridFMaxRec | √ | X | √ | √
√ | Grid underfrequency recovery point | GridFreqMinRecover | 1010 | U16 | 2 | 4000-6000 | 0.01Hz |  | YES |  | guwDeGridFMinRec | √ | X | √ | √
√ | Grid overvoltage level one protection value (default single level) | GridVoltMax1 | 1011 | U16 | 2 | 1000-4000 | 0.1V |  | YES |  | guwDeGridVMax1 | √ | X | √ | √
√ | Grid overvoltage level one protection time (default single level) | GridVoltMaxTime1 | 1012 | U16 | 2 | 0-30000(All Protection) | 0.01S |  | YES |  | guwDeGridVMaxTime1 | √ | X | √ | √
√ | Grid undervoltage first-level protection value (default single level) | GridVoltMin1 | 1013 | U16 | 2 | 500-3000 | 0.1V |  | YES |  | guwDeGridVMin1 | √ | X | √ | √
√ | Grid undervoltage first-level protection time (default single level) | GridVoltMinTime1 | 1014 | U16 | 2 | 0-30000(All Protection) | 0.01S |  | YES |  | guwDeGridVMinTime1 | √ | X | √ | √
√ | Grid overvoltage secondary protection value | GridVoltMax2 | 1015 | U16 | 2 | 1000-4000 | 0.1V |  | YES |  | guwDeGridVMax2 | √ | X | √ | √
√ | Grid overvoltage secondary protection time | GridVoltMaxTime2 | 1016 | U16 | 2 | 0-30000(All Protection) | 0.01S |  | YES |  | guwDeGridVMaxTime2 | √ | X | √ | √
√ | Grid undervoltage secondary protection value | GridVoltMin2 | 1017 | U16 | 2 | 500-3000 | 0.1V |  | YES |  | guwDeGridVMin2 | √ | X | √ | √
√ | Grid undervoltage secondary protection time | GridVoltMinTime2 | 1018 | U16 | 2 | 0-30000(All Protection) | 0.01S |  | YES |  | guwDeGridVMinTime2 | √ | X | √ | √
√ | Grid overvoltage three-level protection value | GridVoltMax3 | 1019 | U16 | 2 | 1000-4000 | 0.1V |  | YES |  | guwDeGridVMax3 | √ | X | √ | √
√ | Grid overvoltage level three protection time | GridVoltMaxTime3 | 1020 | U16 | 2 | 0-30000(All Protection) | 0.01S |  | YES |  | guwDeGridVMaxTime3 | √ | X | √ | √
√ | Grid undervoltage three-level protection value | GridVoltMin3 | 1021 | U16 | 2 | 500-3000 | 0.1V |  | YES |  | guwDeGridVMin3 | √ | X | √ | √
√ | Grid undervoltage level 3 protection time | GridVoltMinTime3 | 1022 | U16 | 2 | 0-30000(All Protection) | 0.01S |  | YES |  | guwDeGridVMinTime3 | √ | X | √ | √
√ | Grid overvoltage level four protection value | GridVoltMax4 | 1023 | U16 | 2 | 1000-4000 | 0.1V |  | YES |  | guwDeGridVMax4 | √ | X | √ | √
√ | Grid overvoltage level 4 protection time | GridVoltMaxTime4 | 1024 | U16 | 2 | 0-30000(All Protection) | 0.01S |  | YES |  | guwDeGridVMaxTime4 | √ | X | √ | √
√ | Grid undervoltage level four protection value | GridVoltMin4 | 1025 | U16 | 2 | 500-3000 | 0.1V |  | YES |  | guwDeGridVMin4 | √ | X | √ | √
√ | Grid undervoltage level 4 protection time | GridVoltMinTime4 | 1026 | U16 | 2 | 0-30000(All Protection) | 0.01S |  | YES |  | guwDeGridVMinTime4 | √ | X | √ | √
√ | Grid overvoltage five-level protection value | GridVoltMax5 | 1027 | U16 | 2 | 1000-4000 | 0.1V |  | YES |  | guwDeGridVMax5 | √ | X | √ | √
√ | Grid overvoltage level five protection time | GridVoltMaxTime5 | 1028 | U16 | 2 | 0-30000(All Protection) | 0.01S |  | YES |  | guwDeGridVMaxTime5 | √ | X | √ | √
√ | Grid undervoltage five-level protection value | GridVoltMin5 | 1029 | U16 | 2 | 500-3000 | 0.1V |  | YES |  | guwDeGridVMin5 | √ | X | √ | √
√ | Grid undervoltage level five protection time | GridVoltMinTime5 | 1030 | U16 | 2 | 0-30000(All Protection) | 0.01S |  | YES |  | guwDeGridVMinTime5 | √ | X | √ | √
√ | "Power grid overfrequency first-level protection value (default single level)" | GridFreqMax1 | 1031 | U16 | 2 | 5000-7000 | 0.01Hz |  | YES |  | guwDeGridFMax1 | √ | X | √ | √
√ | "Power grid overfrequency first-level protection time (default single level)" | GridFreqMaxTime1 | 1032 | U16 | 2 | 0-30000(All Protection) | 0.01S |  | YES |  | guwDeGridFMaxTime1 | √ | X | √ | √
√ | "Power grid underfrequency first-level protection value (default single level)"） | GridFreqMin1 | 1033 | U16 | 2 | 4000-6000 | 0.01Hz |  | YES |  | guwDeGridFMin1 | √ | X | √ | √
√ | "Power grid underfrequency first-level protection time (default single level)" | GridFreqMinTime1 | 1034 | U16 | 2 | 0-30000(All Protection) | 0.01S |  | YES |  | guwDeGridFMinTime1 | √ | X | √ | √
√ | Grid overfrequency secondary protection value | GridFreqMax2 | 1035 | U16 | 2 | 5000-7000 | 0.01Hz |  | YES |  | guwDeGridFMax2 | √ | X | √ | √
√ | Grid overfrequency secondary protection time | GridFreqMaxTime2 | 1036 | U16 | 2 | 0-30000(All Protection) | 0.01S |  | YES |  | guwDeGridFMaxTime2 | √ | X | √ | √
√ | Grid underfrequency secondary protection value | GridFreqMin2 | 1037 | U16 | 2 | 4000-6000 | 0.01Hz |  | YES |  | guwDeGridFMin2 | √ | X | √ | √
√ | Grid underfrequency secondary protection time | GridFreqMinTime2 | 1038 | U16 | 2 | 0-30000(All Protection) | 0.01S |  | YES |  | guwDeGridFMinTime2 | √ | X | √ | √
√ | Grid overfrequency three-level protection value | GridFreqMax3 | 1039 | U16 | 2 | 5000-7000 | 0.01Hz |  | YES |  | guwDeGridFMax3 | √ | X | √ | √
√ | Grid overfrequency level three protection time | GridFreqMaxTime3 | 1040 | U16 | 2 | 0-30000(All Protection) | 0.01S |  | YES |  | guwDeGridFMaxTime3 | √ | X | √ | √
√ | Grid underfrequency three-level protection value | GridFreqMin3 | 1041 | U16 | 2 | 4000-6000 | 0.01Hz |  | YES |  | guwDeGridFMin3 | √ | X | √ | √
√ | Grid underfrequency level 3 protection time | GridFreqMinTime3 | 1042 | U16 | 2 | 0-30000(All Protection) | 0.01S |  | YES |  | guwDeGridFMinTime3 | √ | X | √ | √
√ | Grid overfrequency four-level protection value | GridFreqMax4 | 1043 | U16 | 2 | 5000-7000 | 0.01Hz |  | YES |  | guwDeGridFMax4 | √ | X | √ | √
√ | Grid overfrequency level 4 protection time | GridFreqMaxTime4 | 1044 | U16 | 2 | 0-30000 | 0.01S |  | YES |  | guwDeGridFMaxTime4 | √ | X | √ | √
√ | Grid underfrequency level four protection value | GridFreqMin4 | 1045 | U16 | 2 | 4000-6000 | 0.01Hz |  | YES |  | guwDeGridFMin4 | √ | X | √ | √
√ | Grid underfrequency level 4 protection time | GridFreqMinTime4 | 1046 | U16 | 2 | 0-30000 | 0.01S |  | YES |  | guwDeGridFMinTime4 | √ | X | √ | √
√ | Power grid overfrequency five-level protection value | GridFreqMax5 | 1047 | U16 | 2 | 5000-7000 | 0.01Hz |  | YES |  | guwDeGridFMax5 | √ | X | √ | √
√ | Grid overfrequency five-level protection time | GridFreqMaxTime5 | 1048 | U16 | 2 | 0-30000 | 0.01S |  | YES |  | guwDeGridFMaxTime5 | √ | X | √ | √
√ | Grid underfrequency five-level protection value | GridFreqMin5 | 1049 | U16 | 2 | 4000-6000 | 0.01Hz |  | YES |  | guwDeGridFMin5 | √ | X | √ | √
√ | Grid underfrequency level five protection time | GridFreqMinTime5 | 1050 | U16 | 2 | 0-30000 | 0.01S |  | YES |  | guwDeGridFMinTime5 | √ | X | √ | √
√ | 10-minute average voltage protection value | 10minGridVoltMax | 1051 | U16 | 2 | 1000-4000 | 0.1V |  | YES |  | guwDe10minGridVMax | √ | X | √ | √
√ | 10-minute average voltage recovery value | 10minGridVoltMaxRecover | 1052 | U16 | 2 | 1000-4000 | 0.1V |  | YES |  | guwDe10minGridVMaxRec | √ | X | √ | √
√ | Insulation resistance lower limit | IsoResMin | 1053 | U16 | 2 | 10-800 | KΩ |  | YES |  | guwDeIsoResMin | √ | X | √ | √
| Reserve | Reserve | 1054-1075
√ | Ten minutes overvoltage protection time | 10minGridVoltMaxTime | 1076 | U16 | 2 | 0~65000 | 0.01 |  |  |  |  | √ | √ | √ | √
| Reserve | Reserve | 1077-1499
Setting Parameter 4 (power grid dispatch parameter 1)
√ | Reactive power threshold | NormReactPower | 1500-1501 | U32 | 4 | 0-200000 | VA |  | YES |  | glDeNormReactPwr | √ | X | √ | √
√ | Active output limit | OutPwrMaxPer | 1502 | U16 | 2 | 0-1000 | 0.1% |  | YES |  | guwDeOutPwrMaxPer | √ | X | √ | √
√ | Maximum active output power | OutPwrMax | 1503-1504 | U32 | 4 | 0-200000 | W |  | YES |  | gulDeOutPwrMax | √ | X | √ | √
√ | Reactive power control | QMode | 1551 | U16 | 2 | 0：disable 1：Q Set(CooperateP1552~1554) 2：Pf Set(CooperateP1555) 3：Q By V(CooperateP1556~1563) 4：Pf By P(CooperateP1564~1574) 5：Q By P((CooperateP1587~1594) |  |  | YES |  | guwDeQMode | √ | X | √ | √
√ | Reactive power setting % | QSet% | 1552 | S16 | 2 | (-1000~1000) | 0.001 |  |  |  | gwDeQPerSet | √ | X | √ | √
√ | Reactive power settings | QSet | 1553-1554 | S32 | 4 | ‘-200000~200000 | VA |  | YES |  | glDeQSet | √ | X | √ | √
√ | Power factor setting | PfSet | 1555 | S16 | 2 | (-1000~-800,800~1000) | 0.001 | V1<V2<V3<V4 | YES |  | gwDePfSet | √ | X | √ | √
Setting Parameter 5 (grid dispatch parameter 2)
√ | DRMModel | DRMModel | 2032 | U16 | 2 | 1~9：DRM0~8 ; Other values are invalid |  |  | YES |  | guwDeDRMModel | √ | X | √ | √
√ | DRMPLimit | DRMPLimit | 2033 | S16 | 2 | -1000-+1000 | 0.1% |  | YES |  | gwDeDRMPLimit | √ | X | √ | √
√ | DRMPFSet | DRMPFSet | 2034 | S16 | 2 | （-1000,-800)U(800,1000) | 0.001 |  | YES |  | gwDeDRMPFSet | √ | X | √ | √
√ | Initial connection time | IniConnecT | 2037 | U16 | 2 | 1-2000 | S |  |  |  | guwDeIniConnecT | √ | X | √ | √
√ | Failure reconnection time | ReConnecT | 2038 | U16 | 2 | 20-2000 | S |  | YES |  | guwDeReConnecT | √ | X | √ | √
√ | Feeder network power limit value | GridFeedPlimit | 2039-2040 | S32 | 4 | 0~2147483647 | W |  | YES |  | glDeGridFeedPlimit | √ | X | √ | √
√ | Grid power limit power value | GridBackPlimit | 2041-2042 | S32 | 4 | -2147483648~0 | W |  |  |  | glDeGridBackPlimit | √ | X | √ | √
√ | soft slope | SoftStartSlope | 2043 | U16 | 2 | 0-1000 | 0.10%/min | Grid-connected soft starting slope | YES |  | guwDeSoftStartSlope | √ | X | √ | √
√ | Power ramp up slope | SoftIncSlope | 2044 | U16 | 2 | 0-1000 | 0.10%/min |  |  |  | guwDeSoftIncSlope | √ | X | √ | √
√ | Power ramp down slope | SoftDecSlope | 2045 | U16 | 2 | 0-1000 | 0.10%/min |  |  |  | guwDeSoftDecSlope | √ | X | √ | √
√ | Feeder on-grid power limiting percentage | GridFeedPlimitPer | 2046 | S16 | 2 | 0~32767 | 0.1%
√ | Power grid power limit percentage | GridBackPlimitPer | 2047 | S16 | 2 | --32768~0 | 0.1%
| Reserve | Reserve | 2048-2499 | [8 empty] | √ | X | √ | √
Set parameter 6 (EMS)
√ | EMSMode | EMSMode | 2500 | U16 | 2 | 0: Self-use/SelfUse 1: Charging priority/CharFst 2: Priority in selling electricity/SellFst 3:Battery maintenance/Maintain 4: Command mode/CmdChar 5:External EMS/ExtEms 6: Peak Shaving Mode/PeakShave 7: Imbalance compensation/UbSelfUse 8:Q compensation mode/QSelfUse |  | default：0:SelfUse PeakShave、UbSelfUse、QSe1fUse | YES |  | guwDeEMSMode | √ | X | √ | √
√ | Charge and discharge instructions | ChgCmd | 2501 | U16 | 2 | 0xAA:charge-discharge 0xBB:Stop |  | default：0xBB:stop | NO |  | guwDeChgCmd | √ | X | √ | √
√ | Charge and discharge power instructions | ChgPowerSet | 2502-2503 | S32 | 4 | [-22000,20000] | W | default：0W | NO | Change "charging and discharging power" to "charging and discharging power command"; 21.08.30 Update Unit | glDeChgPowerSet | √ | X | √ | √
√ | AC charging power percentage | AcPChgMax | 2504 | U16 | 2 | 0-1000 | 0.1% |  | YES | 21.08.30 Update scope and units | guwDeCurrMaxAcChg | √ | X | √ | √
√ | AC charging maximum SOC | AcSocMaxChg | 2505 | U16 | 2 | 0-1000 | 0.1% |  | YES | Change "maximum charging SOC" to "maximum charging SOC for AC"; Change "SocMaxChg" to "AcSocMaxChg"; 21.08.30 Update scope and units | guwDeSocMaxChg | √ | X | √ | √
√ | Forced discharge minimum SOC | SocMaxDisChg | 2506 | U16 | 2 | 0-1000 | 0.1% |  | YES | Change "minimum discharge SOC" to "minimum forced discharge SOC"; 21.08.30 Update scope and units; | guwDeSocMaxDisChg | √ | X | √ | √
√ | Forced charging power percentage | PChgMax | 2507 | U16 | 2 | 0-1000 | 0.1% |  | YES | 21.08.30 Update scope and units | guwDePChgMax | √ | X | √ | √
√ | Forced charging power percentage | PDisChgMax | 2508 | U16 | 2 | 0-1000 | 0.1% | PV | YES | 21.08.30 Update scope and units | guwDePDisChgMax | √ | X | √ | √
√ | AC charging start time 1 | TimeOnAcChg1 | 2509 | U16 | 2 | H:0-23 M:0-59 |  | Differentiate weekends and workdays based on actual projects | YES |  | guwDeTimeOnAcChg1 | √ | X | √ | √
√ | AC charging end time 1 | TimeOffAcChg1 | 2510 | U16 | 2 | H:0-23 M:0-59 |  |  | YES |  | guwDeTimeOffAcChg1 | √ | X | √ | √
√ | AC charging start time 2 | TimeOnAcChg2 | 2511 | U16 | 2 | H:0-23 M:0-59 |  |  | YES |  | guwDeTimeOnAcChg2 | √ | X | √ | √
√ | AC charging end time 2 | TimeOffAcChg2 | 2512 | U16 | 2 | H:0-23 M:0-59 |  |  | YES |  | guwDeTimeOffAcChg2 | √ | X | √ | √
√ | AC charging start time 3 | TimeOnAcChg3 | 2513 | U16 | 2 | H:0-23 M:0-59 |  |  | YES |  | guwDeTimeOnAcChg3 | √ | X | √ | √
√ | AC charging end time 3 | TimeOffAcChg3 | 2514 | U16 | 2 | H:0-23 M:0-59 |  |  | YES |  | guwDeTimeOffAcChg3 | √ | X | √ | √
√ | AC charging start time 4 | TimeOnAcChg4 | 2515 | U16 | 2 | H:0-23 M:0-59 |  |  |  |  | guwDeTimeOnAcChg4 | √ | X | √ | √
√ | AC charging end time 4 | TimeOffAcChg4 | 2516 | U16 | 2 | H:0-23 M:0-59 |  |  |  |  | guwDeTimeOffAcChg4 | √ | X | √ | √
√ | Forced charging start time 1 | TimeOnForceChg1 | 2517 | U16 | 2 | H:0-23 M:0-59 |  |  | YES |  | guwDeTimeOnForceChg1 | √ | X | √ | √
√ | Forced charging end time 1 | TimeOffForceChg1 | 2518 | U16 | 2 | H:0-23 M:0-59 |  |  | YES |  | guwDeTimeOffForceChg1 | √ | X | √ | √
√ | Forced charging start time 2 | TimeOnForceChg2 | 2519 | U16 | 2 | H:0-23 M:0-59 |  |  | YES |  | guwDeTimeOnForceChg2 | √ | X | √ | √
√ | Forced charging end time 2 | TimeOffForceChg2 | 2520 | U16 | 2 | H:0-23 M:0-59 |  |  | YES |  | guwDeTimeOffForceChg2 | √ | X | √ | √
√ | Forced charging start time 3 | TimeOnForceChg3 | 2521 | U16 | 2 | H:0-23 M:0-59 |  |  | YES |  | guwDeTimeOnForceChg3 | √ | X | √ | √
√ | Forced charging end time 3 | TimeOffForceChg3 | 2522 | U16 | 2 | H:0-23 M:0-59 |  |  | YES |  | guwDeTimeOffForceChg3 | √ | X | √ | √
√ | Forced charging start time 4 | TimeOnForceChg4 | 2523 | U16 | 2 | H:0-23 M:0-59 |  |  |  |  | guwDeTimeOnForceChg4 | √ | X | √ | √
√ | Forced charging end time 4 | TimeOffForceChg4 | 2524 | U16 | 2 | H:0-23 M:0-59 |  |  |  |  | guwDeTimeOffForceChg4 | √ | X | √ | √
√ | Forced discharge start time 1 | TimeOnForceDisChg1 | 2525 | U16 | 2 | H:0-23 M:0-59 |  |  | YES |  | guwDeTimeOnForceDisChg1 | √ | X | √ | √
√ | Forced discharge end time 1 | TimeOffForceDisChg1 | 2526 | U16 | 2 | H:0-23 M:0-59 |  |  | YES |  | guwDeTimeOffForceDisChg1 | √ | X | √ | √
√ | Forced discharge start time 2 | TimeOnForceDisChg2 | 2527 | U16 | 2 | H:0-23 M:0-59 |  |  | YES |  | guwDeTimeOnForceDisChg2 | √ | X | √ | √
√ | Forced discharge end time 2 | TimeOffForceDisChg2 | 2528 | U16 | 2 | H:0-23 M:0-59 |  |  | YES |  | guwDeTimeOffForceDisChg2 | √ | X | √ | √
√ | Forced discharge start time 3 | TimeOnForceDisChg3 | 2529 | U16 | 2 | H:0-23 M:0-59 |  |  | YES |  | guwDeTimeOnForceDisChg3 | √ | X | √ | √
√ | Forced discharge end time 3 | TimeOffForceDisChg3 | 2530 | U16 | 2 | H:0-23 M:0-59 |  |  | YES |  | guwDeTimeOffForceDisChg3 | √ | X | √ | √
√ | Forced discharge start time 4 | TimeOnForceDisChg4 | 2531 | U16 | 2 | H:0-23 M:0-59 |  |  |  |  | guwDeTimeOnForceDisChg4 | √ | X | √ | √
√ | Forced discharge end time 4 | TimeOffForceDisChg4 | 2532 | U16 | 2 | H:0-23 M:0-59 |  |  |  |  | guwDeTimeOffForceDisChg4 | √ | X | √ | √
√ | Discharge prohibition start time 1 | TimeOnForbidChg1 | 2533 | U16 | 2 | H:0-23 M:0-59 |  |  | YES |  | guwDeTimeOnForbidChg1 | √ | X | √ | √
√ | Discharge prohibited end time 1 | TimeOffForbidChg1 | 2534 | U16 | 2 | H:0-23 M:0-59 |  |  | YES |  | guwDeTimeOffForbidChg1 | √ | X | √ | √
√ | Discharge prohibition start time 2 | TimeOnForbidChg2 | 2535 | U16 | 2 | H:0-23 M:0-59 |  |  | YES |  | guwDeTimeOnForbidChg2 | √ | X | √ | √
√ | Discharge prohibited end time 2 | TimeOffForbidChg2 | 2536 | U16 | 2 | H:0-23 M:0-59 |  |  | YES |  | guwDeTimeOffForbidChg2 | √ | X | √ | √
√ | Discharge prohibition start time 3 | TimeOnForbidChg3 | 2537 | U16 | 2 | H:0-23 M:0-59 |  |  | YES |  | guwDeTimeOnForbidChg3 | √ | X | √ | √
√ | Discharge prohibited end time 3 | TimeOffForbidChg3 | 2538 | U16 | 2 | H:0-23 M:0-59 |  |  | YES |  | guwDeTimeOffForbidChg3 | √ | X | √ | √
√ | Discharge prohibition start time 4 | TimeOnForbidChg4 | 2539 | U16 | 2 | H:0-23 M:0-59 |  |  |  |  | guwDeTimeOnForbidChg4 | √ | X | √ | √
√ | Discharge prohibited end time 4 | TimeOffForbidChg4 | 2540 | U16 | 2 | H:0-23 M:0-59 |  |  |  |  | guwDeTimeOffForbidChg4 | √ | X | √ | √
√ | ForceSocMaxChg | ForceSocMaxChg | 2548 | U16 | 2 | 0-1000 | 0.1% |  | YES | 21.08.30 Update scope and units | guwForceSocMaxChg | √ | X | √ | √
| Reserve | Reserve | 2549-2550 | [8 empty] | √ | X | √ | √
√ | 柴发控制 | GenCtrlEn | 2551 | U16 | 2 | bit0:Diesel engine timing function (0-disable, 1-enable) bit1:Ambient temperature start (0-off, 1-on) bit2:Overload start (0-shutdown, 1-start) bit3-bit16:Rsvd | [5 empty] | √ | X | √ | √
√ | Diesel power generation control | StartGenSocMin | 2552 | U16 | 2 | 0-1000 | 0.1% |  |  |  |  | √ | X | √ | √
√ | Diesel power generation exiting maximum SOC | EndGenSocMax | 2553 | U16 | 2 | 0-1000 | 0.1% |  |  |  |  | √ | X | √ | √
√ | Starting time for diesel power generation 1 | TimeOnGen1 | 2554 | U16 | 2 | H:0-23 M:0-59 | [5 empty] | √ | X | √ | √
√ | Diesel power generation exit time 1 | TimeOffGen1 | 2555 | U16 | 2 | H:0-23 M:0-59 | [5 empty] | √ | X | √ | √
√ | Starting time for diesel power generation 2 | TimeOnGen2 | 2556 | U16 | 2 | H:0-23 M:0-59 | [5 empty] | √ | X | √ | √
√ | Diesel power generation exit time 2 | TimeOffGen2 | 2557 | U16 | 2 | H:0-23 M:0-59 | [5 empty] | √ | X | √ | √
√ | Starting time for diesel power generation 3 | TimeOnGen3 | 2558 | U16 | 2 | H:0-23 M:0-59 | [5 empty] | √ | X | √ | √
√ | Diesel power generation exit time 3 | TimeOffGen3 | 2559 | U16 | 2 | H:0-23 M:0-59 | [5 empty] | √ | X | √ | √
√ | Starting time for diesel power generation 4 | TimeOnGen4 | 2560 | U16 | 2 | H:0-23 M:0-59 | [5 empty] | √ | X | √ | √
√ | Diesel power generation exit time 4 | TimeOffGen4 | 2561 | U16 | 2 | H:0-23 M:0-59 | [5 empty] | √ | X | √ | √
√ | Diesel generator access delay time | TimeOnDelay | 2562 | U16 | 2 | 0-1000 | S |  |  |  |  | √ | X | √ | √
√ | Diesel power generation exit delay time | TimeOffDelay | 2563 | U16 | 2 | 0-60000 | s |  |  |  |  | √ | X | √ | √
√ | Diesel generator ambient temperature start setting | StartGenTEMP | 2564 | S16 | 2 | -40-60 | ℃ |  |  |  |  | √ | X | √ | √
√ | Diesel generator ambient temperature shutdown setting | EndGenTEMP | 2565 | S16 | 2 | -40-60 | ℃ |  |  |  |  | √ | X | √ | √
√ | Energy saving downtime | ECOModeTimeCnt | 2566 | U16 | 2 | 1-6000 | s |  |  |  |  | √ | X | √ | √
√ | Energy saving downtime power value | ECOModePowerStart | 2567 | S16 | 2 | 0~1000 | W |  |  |  |  | √ | X | √ | √
√ | External EMS mode | ExtEmsMod | 2568 | S16 | 2 | 0: Controlled charge and discharge power (CooperateP2569) 1: Controlled inverter power (CooperateP2570) 2: Controlled grid-connected power (Cooperate2571) | [5 empty] | √ | X | √ | √
√ | Control charging and discharging power | ChargePower | 2569 | S16 | 2
√ | Control inverter power | InvPower | 2570 | S16 | 2
√ | Control grid connected power | GridPower | 2571 | S16 | 2
| Reserve | Reserve | 2568-2999 | [8 empty] | √ | X | √ | √
| Set parameter 7 (battery parameters) | [10 empty] | √ | X | √ | √
√ | Battery type | BatType | 3000 | U16 | 2 | 0：No Battery 1：Lith 2：Lead 3：Simulated |  | default：0: No Battery | YES |  | guwDeBatType | √ | X | √ | √
√ | BatBrand | BatBrand | 3001 | U16 | 2 | BatBrand |  | default：2：IVYHV Can ensure high voltage | YES | 21.08.30 Update scope and units | guwDeBatBrand | √ | X | √ | √
√ | Rated voltage of battery | VBatNorm | 3002 | U16 | 2 | 400-8000 | 0.1V |  | YES | 21.08.30 Update scope and units | guwDeVBatNorm | √ | X | √ | √
√ | Battery capacity | BatCap | 3003 | U16 | 2 | 100~10000 | 0.1Ahr |  | YES | 21.08.30 Update scope and units | guwDeBatCap | √ | X | √ | √
√ | Allow daily charging and discharging times | ChgCntMax | 3004 | U16 | 2 | 1-10 |  |  | YES |  | guwDeChgCntMax | √ | X | √ | √
√ | MaxSOC | MaxSOC | 3005 | U16 | 2 | 0~1000 | 0.1% |  | YES | 21.08.30 Update scope and units | guwDeMaxSOC | √ | X | √ | √
√ | MinSOC | MinSOC | 3006 | U16 | 2 | 0~1000 | 0.1% |  | YES | 21.08.30 Update scope and units | guwDeMinSOC | √ | X | √ | √
√ | Battery overvoltage threshold | VBatMax | 3007 | U16 | 2 | 350~8500 | 0.1V |  | YES | 21.08.30 Update scope and units | guwDeVBatMax | √ | X | √ | √
√ | Battery undervoltage threshold | VBatMin | 3008 | U16 | 2 | 350~8500 | 0.1V |  | YES | 21.08.30 Update scope and units | guwDeVBatMin | √ | X | √ | √
√ | Maximum charging current | CurrMaxChg | 3009 | U16 | 2 | 500~50000 | 0.01A |  | YES | 21.08.30 Update scope and units | guwDeCurrMaxChg | √ | X | √ | √
√ | Maximum discharge current | CurrMaxDisChg | 3010 | U16 | 2 | 500~50000 | 0.01A |  | YES | 21.08.30 Update scope and units | guwDeCurrMaxDisChg | √ | X | √ | √
√ | Battery over temperature threshold | TBatMax | 3011 | S16 | 2 | 250~900 | 0.1℃ |  | YES | 21.08.30 Update scope and units | gwDeTBatMax | √ | X | √ | √
√ | Battery under temperature threshold | TBatMin | 3012 | S16 | 2 | -300~250 | 0.1℃ |  | YES | 21.08.30 Update scope and units | gwDeTBatMin | √ | X | √ | √
√ | Constant voltage charging voltage | VConstVolt | 3013 | U16 | 2 | 350~8500 | 0.1V |  | YES | 21.08.30 Update scope and units | guwDeVConstVolt | √ | X | √ | √
√ | Constant voltage charging termination current | IConstVoltEnd | 3014 | U16 | 2 | 10~10000 | 0.01A |  | YES | 21.08.30 Update scope and units | guwDeIConstVoltEnd | √ | X | √ | √
√ | Constant voltage charging time | TConstVolt | 3015 | U16 | 2 | 1-15000 | S |  | YES | 21.08.30 Update scope and units | guwDeTConstVolt | √ | X | √ | √
√ | Discharge termination voltage | VDisChgEnd | 3016 | U16 | 2 | 350~8000 | 0.1V |  | YES | 21.08.30 Update scope and units | guwDeVDisChgEnd | √ | X | √ | √
√ | Emergency charging start voltage | EmerChgStartV | 3017 | U16 | 2 | 100-8000 | 0.1V |  |  | 21.08.30 Update scope and units | guwDeEmerChgStartV | √ | X | √ | √
√ | Emergency charging stop voltage | EmerChgEndV | 3018 | U16 | 2 | 350-8000 | 0.1V |  |  | 21.08.30 Update scope and units | guwDeEmerChgEndV | √ | X | √ | √
√ | Emergency charging current | EmerChgI | 3019 | U16 | 2 | 100~50000 | 0.01A |  | YES | 21.08.30 Update scope and units | guwDeEmerChgI | √ | X | √ | √
√ | Resistance compensation | BatResComp | 3020 | U16 | 2 | 0.0~50000 | 0.1mΩ |  | YES |  | gwDeBatResComp | √ | X | √ | √
√ | temperature compensation | BatTempComp | 3021 | S16 | 2 | -5000~5000 | (0.1mV/cell/℃ |  | YES | 21.08.30 Update scope and units | gwDeBatTempComp | √ | X | √ | √
√ | Maximum charging power | WChaMax | 3022-3023 | U32 | 4 | 100~500000 | 1W |  | YES | 21.08.30 Update scope and units | gwDeWChaMax | √ | X | √ | √
√ | Maximum charging change rate | WChaGra | 3024 | U16 | 2 | 0~60000 | 0.1%/s |  | YES | 21.08.30 Update scope and units | gwDeWChaGra | √ | X | √ | √
√ | Maximum point change rate | WDisChaGra | 3025 | U16 | 2 | 0~60000 | 0.1%/s |  | YES | 21.08.30 Update scope and units | gwDeWDisChaGra | √ | X | √ | √
√ | Lead acid battery manufacturer | LeadAcidBrand | 3026 | U16 |  | 0. common 1. SACRED 2. |  | default：0：common |  |  |  | √ | X | √ | √
√ | Number of series connections | SeriesPackNum | 3027 | U16 | 2 | 1~25 | [5 empty] | √ | X | √ | √
√ | Rated voltage saving value | VPackNorm | 3028 | U16 | 2 | 60~850 | 0.1V |  |  |  |  | √ | X | √ | √
√ | Voltage saving overvoltage threshold | VPackMax | 3029 | U16 | 2 | 60~850 | 0.1V |  |  |  |  | √ | X | √ | √
√ | Voltage saving undervoltage threshold | VPackMin | 3030 | U16 | 2 | 60~850 | 0.1V |  |  |  |  | √ | X | √ | √
√ | Upper limit of voltage saving charging | VPackChgEnd | 3031 | U16 | 2 | 60~850 | 0.1V |  |  |  |  | √ | X | √ | √
√ | Lower limit of voltage saving discharge | VPackDisChgEnd | 3032 | U16 | 2 | 60~850 | 0.1V |  |  |  |  | √ | X | √ | √
√ | Voltage saving emergency charging start | VPackEmerChgStart | 3033 | U16 | 2 | 60~850 | 0.1V |  |  |  |  | √ | X | √ | √
√ | Emergency charging stop for voltage saving | VPackEmerChgEnd | 3034 | U16 | 2 | 60~850 | 0.1V |  |  |  |  | √ | X | √ | √
√ | Lead acid battery SOC | AcidSoc | 3035 | U16 | 2 | 0-1000 | 0.1% |  |  |  |  | √ | X | √ | √
√ | Minimum SOC for grid connected discharge | Ongrid_Minsoc | 3036 | U16 | 2 | 0~1000 | 0.1% |  |  |  |  | √ | X | √ | √
√ | Reserve | Reserve | 3037-3499 | [8 empty] | √ | X | √ | √
Set parameter 8 (lithium battery communication data, scrolling distribution)
√ | Maximum charging current | ChgCurrMax | 3500-3501 | Float/S32 | 4 | 100-10000 | 0.01A |  | NO |  | gfDeChgCurrMax | √ | X | X | X
√ | Maximum discharge current | DisChgCurrMax | 3502-3503 | Float/S32 | 4 | 100-10000 | 0.01A |  | NO |  | gfDeDisChgCurrMax | √ | X | X | X
√ | Maximum charging SOC | ChgMaxSoc | 3504 | U16 | 2 | 0-100 | % |  | NO |  | guwDeChgMaxSoc | √ | X | X | X
√ | DisChgMinSoc | DisChgMinSoc | 3505 | U16 | 2 | 0-100 | % |  | NO |  | guwDeDisChgMinSoc | √ | X | X | X
√ | Maximum charging voltage | ChgVMax | 3506-3507 | Float/U32 | 4 |  | 0.1V |  |  |  | gfDeChgVMax | √ | X | X | X
√ | Minimum discharge voltage | DisChgVMin | 3508-3509 | Float/U32 | 4 |  | 0.1V |  | NO |  | gfDeDisChgVMin | √ | X | X | X
√ | Battery control command | BatCtrlCmd | 3510 | U16 | 2 | Bit0:Charge Enable Bit1:Discharge enable Bit2:Strong charging instruction Bit3:Power off command |  |  | NO |  | guwDeBatCtrlCmd | √ | X | X | X
√ | Emergency Charging Start SOC | EmerChgStartSoc | 3511 | U16 | 2 |  | % |  |  |  | guwDeEmerChgStartSoc | √ | X | X | X
√ | Emergency charging stop SOC | EmerChgEndSoc | 3512 | U16 | 2 |  | % |  |  |  | guwDeEmerChgEndSoc | √ | X | X | X
√ | Battery status | BatState | 3515 | U16 | 2 |  |  | Sleep, start, run, malfunction |  |  | guwDeBatState | √ | X | X | X
√ | Battery Health State of Health (SOH) | SOH | 3516 | U16 | 2 |  | % |  | NO |  | guwDeSOH | √ | X | X | X
√ | SOC | SOC | 3517 | U16 | 2 |  | % |  | NO |  | guwDeSOC | √ | X | X | X
√ | Battery voltage | BatVolt | 3518-3519 | Float/U32 | 4 |  | 0.1V |  | NO |  | gfDeBatVolt | √ | X | X | X
√ | Battery current | BatCurr | 3520-3521 | Float/S32 | 4 |  | 0.01A | Charging is positive, discharging is negative | NO |  | gfDeBatCurr | √ | X | X | X
√ | Battery temperature | BatTemp | 3522-3523 | Float/U32 | 4 |  | 0.1℃ |  | NO |  | gfDeBatTemp | √ | X | X | X
√ | Minimum individual voltage | VCellMin | 3524-3525 | Float/U32 | 4 |  | mV |  | NO |  | gfDeVCellMin | √ | X | X | X
√ | Maximum individual voltage | VCellMax | 3526-3527 | Float/U32 | 4 |  | mV |  | NO |  | gfDeVCellMax | √ | X | X | X
√ | Battery malfunction | BatErr | 3528-3529 | U32 | 4 | [5 empty] | gulDeBatErr | √ | X | X | X
√ | Reserve | Reserve | 3530-3541 | [8 empty] | √ | X | X | X
√ | Battery hardware version | BatHwVersion | 3542 | U16 | 2 | H: Hardware version V, L: Hardware version R | [5 empty] | √ | X | X | X
√ | Battery software version | BatSwVersion | 3543 | U16 | 2 | H: Software main version, L: software sub version | [5 empty] | √ | X | X | X
√ | Number of battery cells | BatCellNums | 3544 | U16 | 2 | [6 empty] | √ | X | X | X
√ | Reserve | Reserve | 3530-3999 | [8 empty] | √ | X | X | X

## Run function enable
B0:switch machine | Remark
B1:Soft start enable
B2:Power soft
B3:EPS Mode enable
B4:Timing AC charge enable
B5:Timing charge enable
B6:Timing discharge enable
B7:JET simulating test
B8:DRMS enable
B9:ripple control
B10: Grid high voltage drop
B11: Grid Low Voltage Rise
B12: Grid over-frequency and load reduction
B13: Grid under-frequency load increase
B14:HVRT
B15:LVRT
B16:Timing Forbid discharge enable
B17: other17
B18:other18
B19:other19
B20:DisselGenFunction
B21:DieselWorkMode
B22:other22
B23:EcoEn
B24~B31 Reseved

## Protection function enabled
B0:Grid connection range judgment
B1:AactiveIsland
B2:PassiveIsland
B3:OverVolt
B4:UnderVolt
B5:OverFreq
B6:UnderFreq
B7:10minOverVolt
B8:IsoChk
B9:DciChk
B10:GfciChk
B11:EarthChk
B12:Three-phase unbalance
B13:Power grid transient voltage protection
B14:Bus midpoint unbalance protection
B15:PV Reverse connection
B16:PV Abnormal
B17:Sampling detection
B18:Abnormal temperature sampling
B19:High and low temperature protection
B20:GEN voltage frequency detection
B21:Relay detection
B22:Internal communication detection
B23:Fan detection
B24:ammete & CT detection
B25:Afci
B26:RSDEN
B27~B31 Reseved

## Safty
Applicable machine type range: 129-138 (low-voltage version safety regulations) |  | Applicable machine type range: 117-128 (high-voltage version safety regulations) |  | Applicable machine type range: other conditions (normal version of safety regulations)
Value of register address (10 base) | Safty | Value of register address (10 base) | Safty | Value of register address (10 base) | Safty
51 | ComL 50Hz | 151 | ComH 50Hz | 0 | Com-50Hz
52 | ComL 60Hz | 152 | ComH 60Hz | 1 | Com-60Hz
53 | MX | 153 | TW | 2 | China
54 | JP 50Hz | 154 | PH | 3 | Japan-50
55 | JP 60Hz | 155 | SA | 4 | Japan-60
56 | US | 156 | FI | 5 | US_240S
57 | CA | 157 | NL | 6 | US_240D
58 | TW | 158 | NO | 7 | US_208S
59 | HK | 159 | CH | 8 | US_208D
60 | NO | 160 | CZ | 9 | Australia
61 | BH | 161 | CA | 10 | UK_G99
62 | NI | 162 | US | 11 | UK_G98
63 | GT | 163 | BZ | 12 | DE
64 | SA | 164 | CR | 13 | DE_BDEW
65 | KR | 165 | DM | 14 | France
66 | KH | 166 | HN | 15 | Fra-IL50Hz
67 | PH | 167 | JM | 16 | Fra-IL60Hz
68 | VN | 168 | MX | 17 | Poland
69 | LB | 169 | PY | 18 | Italy
70 | EC | 170 | PE | 19 | ThailandME
71 | BR | 171 | CN | 20 | ThailandPE
72 | BB | 172 | EC | 21 | India
73 | BS | 173 | PA | 22 | SouthKorea
74 | JM | 174 | Reserve174 | 23 | Philippin
75 | CU | 175 | Reserve175 | 24 | DPRK
76 | DM | 176 | Reserve176 | 25 | Malaysia
77 | BM | 177 | Reserve177 | 26 | Cyprus
78 | HN | 178 | Reserve178 | 27 | Holland
79 | BZ | 179 | Reserve179 | 28 | EN50549-1
80 | VE | 180 | Reserve180 | 29 | Spain
81 | PR | 181 | Reserve181 | 30 | Greece
82 | BO | 182 | Reserve182 | 31 | Hungary
83 | CO | 183 | Reserve183 | 32 | Portugal
84 | CR | 184 | Reserve184 | 33 | Belgium
85 | HT |  |  | 34 | Denmark
86 | GY |  |  | 35 | Estonia
87 | SV |  |  | 36 | Moldova
88 | GU |  |  | 37 | Slovak
89 | SR |  |  | 38 | Sweden
90 | ES |  |  | 39 | Austria
91 | MA |  |  | 40 | Bulgaria
92 | LY |  |  | 41 | Croatia
93 | ML |  |  | 42 | Ukraine
94 | SN |  |  | 43 | S.Africa
95 | LR |  |  | 44 | Mauritius
96 | CONNERA |  |  | 45 | Israel
97 | CN |  |  | 46 | Mexico
98 | Reserve98 |  |  | 47 | Brazil
99 | Reserve99 |  |  | 48 | SriLanka
100 | Reserve100 |  |  | 49 | Chile
101 | Reserve101 |  |  | 50 | CONNERA
102 | Reserve102 |  |  | 251 | Ireland
103 | Reserve103 |  |  | 252 | Lithuania
104 | Reserve104 |  |  | 253 | Slovenia
105 | Reserve105 |  |  | 254 | Latvia
106 | Reserve106 |  |  | 255 | IEC 61727
107 | Reserve107 |  |  | 256 | Colombia
108 | Reserve108 |  |  | 257 | Romania
|  |  |  | 258 | Norway
|  |  |  | 259 | Reserve259
|  |  |  | 260 | Reserve260
|  |  |  | 261 | Reserve261
|  |  |  | 262 | Reserve262
|  |  |  | 263 | Reserve263
|  |  |  | 264 | Reserve264
|  |  |  | 265 | Reserve265
|  |  |  | 266 | Reserve266
|  |  |  | 267 | Reserve267
|  |  |  | 268 | Reserve268
|  |  |  | 269 | Reserve269
|  |  |  | 270 | Reserve270
|  |  |  | 271 | Reserve271
|  |  |  | 272 | Reserve272

## BatBrand
Value of register address | enum
(10 base）
0 | Afore
1 | PYLON
2 | IVY
3 | JBS
4 | Taoke
5 | HSD
6 | Taisu
7 | Rita
8 | Soluna
9 | HYS
10 | Wanke
11 | SunWoda
12 | Sunplus
13 | Dyness
14 | UZ
15 | Pytes
16 | Vision
17 | Aoboet
18 | Taico
19 | CALB
20 | Oliter
21 | Apollo
22 | SolarWatt
23 | Flash
24 | Tectronic
25 | FEB
26 | CFE
27 | ATVT
28 | Homenergon
29 | Ampace
30 | Voltsmile
31 | Livoltek
32 | Vestwood
33 | Johnray
34 | HuaXing
35 | Austa
36 | ZRGP
37 | Dowell
38 | RK
39 | Hanersun
40 | AlpSolarr
41 | DMEGC
42 | Genixgreen
43 | HaierNAHUI
44 | San Rase
45 | FZSoNick
46 | KNYEE
47 | Hailei
48 | Svolt
49 | Afore_H
50 | OthPL
51 | Reserve51
52 | Reserve52
53 | Reserve53
54 | Reserve54
55 | Reserve55
56 | Reserve56
57 | Reserve57
58 | Reserve58
59 | Reserve59
60 | Reserve60
61 | Reserve61
62 | Reserve62
63 | Reserve63
64 | Reserve64
65 | Reserve65
66 | Reserve66
67 | Reserve67
68 | Reserve68

## fault list
Fault Type | Serial Number | bit | Fault code | Fault code
PV failure
| 1 | 0 | A01 | PvConnectFault
| 2 | 1 | A02 | IsoFault
| 3 | 2 | A03 | PvAfciFault
| 4 | 3 | A04 | Pv1OverVoltageFault
| 5 | 4 | A05 | Pv2OverVoltageFault
| 6 | 5 | A06 | Pv3OverVoltageFault
| 7 | 6 | A07 | Pv4OverVoltageFault
| 8 | 7 | A08 | Pv5OverVoltageFault
| 9 | 8 | A09 | Pv6OverVoltageFault
| 10 | 9 | A10 | Pv7OverVoltageFault
| 11 | 10 | A11 | Pv8OverVoltageFault
| 12 | 11 | A12 | Pv9OverVoltageFault
| 13 | 12 | A13 | Pv10OverVoltageFault
| 14 | 13 | A14 | Pv11OverVoltageFault
| 15 | 14 | A15 | Pv12OverVoltageFault
| 16 | 15 | A16 | PV1ReverseFault
| 17 | 16 | A17 | PV2ReverseFault
| 18 | 17 | A18 | PV3ReverseFault
| 19 | 18 | A19 | PV4ReverseFault
| 20 | 19 | A20 | PV5ReverseFault
| 21 | 20 | A21 | PV6ReverseFault
| 22 | 21 | A22 | PV7ReverseFault
| 23 | 22 | A23 | PV8ReverseFault
| 24 | 23 | A24 | PV9ReverseFault
| 25 | 24 | A25 | PV10ReverseFault
| 26 | 25 | A26 | PV11ReverseFault
| 27 | 26 | A27 | PV12ReverseFault
| 28 | 27 | A28
| 29 | 28 | A29
| 30 | 29 | A30
| 31 | 30 | A31
| 32 | 31 | A32
| 33 | 0 | A33 | Pv1AberrantFault
| 34 | 1 | A34 | Pv2AberrantFault
| 35 | 2 | A35 | Pv3AberrantFault
| 36 | 3 | A36 | Pv4AberrantFault
| 37 | 4 | A37 | Pv5AberrantFault
| 38 | 5 | A38 | Pv6AberrantFault
| 39 | 6 | A39 | Pv7AberrantFault
| 40 | 7 | A40 | Pv8AberrantFault
| 41 | 8 | A41 | Pv9AberrantFault
| 42 | 9 | A42 | Pv10AberrantFault
| 43 | 10 | A43 | Pv11AberrantFault
| 44 | 11 | A44 | Pv12AberrantFault
| 45 | 12 | A45 | Pv13AberrantFault
| 46 | 13 | A46 | Pv14AberrantFault
| 47 | 14 | A47 | Pv15AberrantFault
| 48 | 15 | A48 | Pv16AberrantFault
| 49 | 16 | A49 | Pv17AberrantFault
| 50 | 17 | A50 | Pv18AberrantFault
| 51 | 18 | A51 | Pv19AberrantFault
| 52 | 19 | A52 | Pv20AberrantFault
| 53 | 20 | A53 | Pv21AberrantFault
| 54 | 21 | A54 | Pv22AberrantFault
| 55 | 22 | A55 | Pv23AberrantFault
| 56 | 23 | A56 | Pv24AberrantFault
battery failure
| 1 | 0 | B01 | PcsBatVolOverFault
| 2 | 1 | B02 | PcsBatVolUnderFault
| 3 | 2 | B03 | PcsBatVolInsOverFaul
| 4 | 3 | B04 | PcsBatReverseFault
| 5 | 4 | B05 | PcsBatConnectFault
| 6 | 5 | B06 | PcsBatCommunicationF
| 7 | 6 | B07 | PcsBatTempSensorOpen
| 8 | 7 | B08 | PcsBatTempSensorShor
| 9 | 8 | B09 | BmsBatSystemFault
| 10 | 9 | B10 | BmsBatVolOverFault
| 11 | 10 | B11 | BmsBatVolUnderFault
| 12 | 11 | B12 | BmsCellVolOverFault
| 13 | 12 | B13 | BmsCellVolUnderFault
| 14 | 13 | B14 | BmsCellVolUnbanceFau
| 15 | 14 | B15 | BatChgCurOverFault
| 16 | 15 | B16 | BatDChgCurOverFault
| 17 | 16 | B17 | BatTemperatureOverFa
| 18 | 17 | B18 | BatTemperatureUnderF
| 19 | 18 | B19 | CelTemperatureOverFa
| 20 | 19 | B20 | CelTemperatureUnderF
| 21 | 20 | B21 | BatIsoFault
| 22 | 21 | B22 | BatSocLowFault
| 23 | 22 | B23 | BmsInterComFault
| 24 | 23 | B24 | BatRelayFault
| 25 | 24 | B25 | BatPreChaFault
| 26 | 25 | B26 | BmsBatChgMosFault
| 27 | 26 | B27 | BmsBatDChgMosFault
| 28 | 27 | B28 | BMSVolOVFault
| 29 | 28 | B29 | BMSVolLFault
| 30 | 29 | B30 | VolLockOpenFault
| 31 | 30 | B31 | VolLockShortFault
| 32 | 31 | B32 | ChgRefOVFault
grid fault
| 1 | 0 | C01 | GridLossFault
| 2 | 1 | C02 | GridVoltUnbalanFault
| 3 | 2 | C03 | GridInstVoltHighFaul
| 4 | 3 | C04 | Grid10MinOverFault
| 5 | 4 | C05 | GridOverVoltFault
| 6 | 5 | C06 | GridUnderVoltFault
| 7 | 6 | C07 | GridOverLineVoltFaul
| 8 | 7 | C08 | GridUnderLineVoltFau
| 9 | 8 | C09 | GridOverFreqFault
| 10 | 9 | C10 | GridUnderFreqFault
Off grid fault
| 1 | 0 | D01 | UpsOVerPowerFault
| 2 | 1 | D02 | GridConflictFault
| 3 | 2 | D03 | DieselOverVoltFault
| 4 | 3 | D04 | DieselUnderVoltFault
| 5 | 4 | D05 | DieselOverFreqFault
| 6 | 5 | D06 | DieselUnderFreqFault
DC side fault
| 1 | 0 | E01 | Pv1HwOverCurrFault
| 2 | 1 | E02 | Pv2HwOverCurrFault
| 3 | 2 | E03 | Pv3HwOverCurrFault
| 4 | 3 | E04 | Pv4HwOverCurrFault
| 5 | 4 | E05 | Pv5HwOverCurrFault
| 6 | 5 | E06 | Pv6HwOverCurrFault
| 7 | 6 | E07 | Pv7HwOverCurrFault
| 8 | 7 | E08 | Pv8HwOverCurrFault
| 9 | 8 | E09 | Pv9HwOverCurrFault
| 10 | 9 | E10 | Pv10HwOverCurrFault
| 11 | 10 | E11 | Pv11HwOverCurrFault
| 12 | 11 | E12 | Pv12HwOverCurrFault
| 13 | 12 | E13 | Pv1SwOverCurrFault
| 14 | 13 | E14 | Pv2SwOverCurrFault
| 15 | 14 | E15 | Pv3SwOverCurrFault
| 16 | 15 | E16 | Pv4SwOverCurrFault
| 17 | 16 | E17 | Pv5SwOverCurrFault
| 18 | 17 | E18 | Pv6SwOverCurrFault
| 19 | 18 | E19 | Pv7SwOverCurrFault
| 20 | 19 | E20 | Pv8SwOverCurrFault
| 21 | 20 | E21 | Pv9SwOverCurrFault
| 22 | 21 | E22 | Pv10SwOverCurrFault
| 23 | 22 | E23 | Pv11SwOverCurrFault
| 24 | 23 | E24 | Pv12SwOverCurrFault
| 25 | 24 | E25
| 26 | 25 | E26
| 27 | 26 | E27
| 28 | 27 | E28
| 29 | 28 | E29
| 30 | 29 | E30
| 31 | 30 | E31
| 32 | 31 | E32
| 33 | 0 | E33 | Boost1SelfCheckFault
| 34 | 1 | E34 | Boost2SelfCheckFault
| 35 | 2 | E35 | Boost3SelfCheckFault
| 36 | 3 | E36 | Boost4SelfCheckFault
| 37 | 4 | E37 | Boost5SelfCheckFault
| 38 | 5 | E38 | Boost6SelfCheckFault
| 39 | 6 | E39 | Boost7SelfCheckFault
| 40 | 7 | E40 | Boost8SelfCheckFault
| 41 | 8 | E41 | Boost9SelfCheckFault
| 42 | 9 | E42 | Boost10SelfCheckFault
| 43 | 10 | E43 | Boost11SelfCheckFault
| 44 | 11 | E44 | Boost12SelfCheckFault
| 45 | 12 | E45 | BusAllVoltHwOveFault
| 46 | 13 | E46 | BusHalfVoltHwOveFault
| 47 | 14 | E47 | BusAllVoltSwOveFault
| 48 | 15 | E48 | BusHalfVoltSwOveFault
| 49 | 16 | E49 | BusAllVoltSwUnderFault
| 50 | 17 | E50 | BusUnbalaFault
| 51 | 18 | E51 | BusBalBridgeHwOverCurFault
| 52 | 19 | E52 | BusBalBridgeSwOverCurFault
| 53 | 20 | E53 | BusBalBridgeSelfCheckFault
| 54 | 21 | E54 | BuckBoostHwOverCurrFault
| 55 | 22 | E55 | BuckBoostSwOverCurrFault
| 56 | 23 | E56 | BuckBoostSelfCheckFault
| 57 | 24 | E57 | BuckBoostSwOverVoltFault
| 58 | 25 | E58 | HwTransformerFault
| 59 | 26 | E59 | BdcFuseFault
| 60 | 27 | E60 | BdcRelayFault
AC side fault
| 1 | 0 | F01 | HardwareFault
| 2 | 1 | F02 | InvHwCurrHighFault
| 3 | 2 | F03 | RInvInstCurrHighFault
| 4 | 3 | F04 | SInvInstCurrHighFault
| 5 | 4 | F05 | TInvInstCurrHighFault
| 6 | 5 | F06 | GridCurrUnbanceFault
| 7 | 6 | F07 | DcInjCurrFault
| 8 | 7 | F08 | LeakCurrFault
| 9 | 8 | F09 | PllFault
| 10 | 9 | F10 | GridRelayFault
| 11 | 10 | F11 | UpsRelayFault
| 12 | 11 | F12 | GenRelayFault
| 13 | 12 | F13 | Relay4Fault
| 14 | 13 | F14 | RUPSInstCurrHighFault
| 15 | 14 | F15 | SUPSInstCurrHighFault
| 16 | 15 | F16 | TUPSInstCurrHighFault
| 17 | 16 | F17 | RDieselInstCurrHighFault
| 18 | 17 | F18 | SDieselInstCurrHighFault
| 19 | 18 | F19 | TDieselInstCurrHighFault
| 20 | 19 | F20 | TDieselPowerBackFault
| 21 | 20 | F21 | UPSInvHighVoltFault
| 22 | 21 | F22 | UPSInvLowVoltFault
| 23 | 22 | F23 | UPSInvHighFreqFault
| 24 | 23 | F24 | UPSInvLowFreqFault
| 25 | 24 | F25 | DcInjVoltFault
system failure
| 1 | 0 | G01 | PV1CurAdChanFault
| 2 | 1 | G02 | PV2CurAdChanFault
| 3 | 2 | G03 | PV3CurAdChanFault
| 4 | 3 | G04 | PV4CurAdChanFault
| 5 | 4 | G05 | PV5CurAdChanFault
| 6 | 5 | G06 | PV6CurAdChanFault
| 7 | 6 | G07 | PV7CurAdChanFault
| 8 | 7 | G08 | PV8CurAdChanFault
| 9 | 8 | G09 | PV9CurAdChanFault
| 10 | 9 | G10 | PV10CurAdChanFault
| 11 | 10 | G11 | PV11CurAdChanFault
| 12 | 11 | G12 | PV12CurAdChanFault
| 13 | 12 | G13 | BDCCurrAdChanFault
| 14 | 13 | G14 | BDCTransCurAdChanFault
| 15 | 14 | G15 | BusBalBridgeCurAdChanFault
| 16 | 15 | G16 | RInvCurAdChanFault
| 17 | 16 | G17 | SInvCurAdChanFault
| 18 | 17 | G18 | TInvCurAdChanFault
| 19 | 18 | G19 | RInvDciAdChanFault
| 20 | 19 | G20 | SInvDciAdChanFault
| 21 | 20 | G21 | TInvDciAdChanFault
| 22 | 21 | G22 | LeakSampCurrChanFault
| 23 | 22 | G23 | VolRefAdChanFault
| 24 | 23 | G24 | RUpsCurAdChanFault
| 25 | 24 | G25 | SUpsCurAdChanFault
| 26 | 25 | G26 | TUpsCurAdChanFault
| 27 | 26 | G27 | RGenCurAdChanFault
| 28 | 27 | G28 | SGenCurAdChanFault
| 29 | 28 | G29 | TGenCurAdChanFault
| 30 | 29 | G30 | RUpsDciAdChanFault
| 31 | 30 | G31 | SUpsDciAdChanFault
| 32 | 31 | G32 | TUpsDciAdChanFault
| 33 | 0 | G33
| 34 | 1 | G34
| 35 | 2 | G35
| 36 | 3 | G36
| 37 | 4 | G37 | TemperatureAdChanFault
| 38 | 5 | G38 | PVBatBusInconsistentFault
| 39 | 6 | G39 | MasterSlaveInconsistentFault
| 40 | 7 | G40 | InconsistentPortVolFault
| 41 | 8 | G41 | EnvironmentTemOverFault
| 42 | 9 | G42 | EnvironmentTemLowFault
| 43 | 10 | G43 | CoolingHighTempFault
| 44 | 11 | G44 | CoolingLowTempFault
| 45 | 12 | G45 | HighTemp3Fault
| 46 | 13 | G46 | LowTemp3Fault
| 47 | 14 | G47 | DspHighTempFault
| 48 | 15 | G48 | SoftHardInconsFault
Permanent Fault | 1 | 0 | H01 | PVCurrOverErr
| 2 | 1 | H02 | BdcCurrOverErr
| 3 | 2 | H03 | InvCurrOverErr
| 4 | 3 | H04 | UpsCurrOverErr
| 5 | 4 | H05 | GenCurrOverErr
| 6 | 5 | H06 | DcInjCurrErr
| 7 | 6 | H07 | DcInjVoltErr
| 8 | 7 | H08 | BusAllVoltSwOveErr
| 9 | 8 | H09 | RelayErr
| 10 | 9 | H10 | PvBoostSelfChckErr
| 11 | 10 | H11 | BDCSelfChkPermErr
| 12 | 11 | H12 | InvOpenTestErr
Internal alarm
| 1 | 0 | I01 | InterFanWarning
| 2 | 1 | I02 | ExternFanWarning
| 3 | 2 | I03 | Fan3Warning
| 4 | 3 | I04 | EnvironmentTemAdChanWarning
| 5 | 4 | I05 | CoolingTemAdChanWarning
| 6 | 5 | I06 | Temp3AdChanWarning
| 7 | 6 | I07 | FlashReadWarning
| 8 | 7 | I08 | EepromComWarning
| 9 | 8 | I09 | SlaveComWarning
| 10 | 9 | I10 | HmiComWarning
| 11 | 10 | I11 | FreqCalcConflictWarning
| 12 | 11 | I12 | UnsetModel
| 13 | 12 | I13 | ArcComWarning
| 14 | 13 | I14 | DspUpdate Fail
| 15 | 14 | I15 | OldTestPwrWarning
| 16 | 15 | I16 | PhsAbnormal
| 17 | 16 | I17 | Fan2Warning
external alarm
| 1 | 0 | J01 | MeterComWarning
| 2 | 1 | J02 | MeterInstalWarning
| 3 | 2 | J03 | SohWarning
| 4 | 3 | J04 | GndAbnormalWarning
| 5 | 4 | J05 | ParallelComWarning
| 6 | 5 | J06 | PVOverVoltWaring
| 7 | 6 | J07 | Meter2ComWarning
| 8 | 7 | J08 | ParaComErr
| 9 | 8 | J09 | ParaComWarning
| 10 | 9 | J10 | MeterDataAbnormal
| 11 | 10 | J11 | CTDirectionErr
| 12 | 11 | J12 | Bat Activate Fail
| 13 | 12 | J13 | BatSocLowWarning

## Agreement Change Description
Mumber | version number | Change details | Change date
1 | V1.0 | edition | 2021-11-06
2 | V1.1 | first edition | 2023-08-06
3 | V1.2 | New categories of grid-connected machines and energy storage machines are added according to customer requirements. "√" is a field that is used, and "×" is a field that is not used. | 2023-10-12
4 | V1.3 | Grid-connected machine fields: PV power generation on the day, PV1 power generation on the day, PV2 power generation on the day, PV3 power generation on the day, PV4 power generation on the day, PV5 power generation on the day, PV6 power generation on the day, total PV power generation, modified from "√" is "×" | 2023-11-22
5 | V1.4 | The resistance compensation data type S16 is modified to U16 | 2023-12-05
"B22:RSSEn" is deleted when the running function is enabled.
When the protection function is enabled, "B26:RSSEn" is changed to "B26:RSDEN"
The data range of grid power limit power value is changed from -200000~0 to -2147483648~0
Grid power limit power percentage data range -1000~0 is modified to -32768~0
The feed on-grid power limit value data range is modified from 0~200000 to 0~2147483647
The feed on-grid power limit percentage 0~1000 is modified to 0~32767
Lithium battery manufacturer update
Added 7 to the battery status of address 2000: Wake Up
The grid-connected discharge depth is modified to the grid-connected discharge minimum SOC, and the GridDod is modified to Ongrid_Minsoc.
Electricity meter manufacturer adds Livoltek-3p and Chint-3p
The initial on-grid time range is changed from 1-600 to 1-2000
Fault reconnection time range changed from 20-600 to 20-2000
Add Safty 258: Norway
Added 10 minute overvoltage protection time (10minGridVoltMaxTime), address 1076
New battery hardware version (BatHwVersion), address 3542
New battery software version (BatSwVersion), address 3543
Set parameter 8 (lithium battery communication data, scrolling distribution) to read-only
Applicable machine type range: 129-137 (low-voltage version safety regulations), 137 is modified to 138