## 1.系统参数
Parameter Name | Read Write | Address (DEC) | Address (HEX) | Unit | Description
Current time - year | RW | 4050 | 0FD2 | / | [2000-2099], set up to write the actual year, set up 2022 on the next 2022, read when the 2000 is included, such as the current year is 2022, read up the data is 2022
Current Time-Month | RW | 4051 | 0FD3 | / | [1-12]
Current time - day | RW | 4052 | 0FD4 | / | [1-31]
Current time - hour | RW | 4053 | 0FD5 | / | [0-23]
Current time-minutes | RW | 4054 | 0FD6 | / | [0-59]
Current time-second | RW | 4055 | 0FD7 | / | [0-59]
Switch On/Off Settings | RW | 20030 | 4E3E | / | 207-On; 206-Off [207]
Device reboot | W | 20031 | 4E3F | / | 0xAA-Device reboot [0x55].
Country Selection | RW | 22310 | 5726 | / | [0-255][6]
Restore Defaults | W | 20050 | 4E52 | / | 0xAA-Restore factory value, other values are invalid
Battery selection | RW | 26101 | 65F5 | / | 0~2 , 0: no battery, 1: lithium battery, 2: battery simulator [0]
DO output function selection | RW | 23275 | 5AEB | / | 0~3, 0: off, 1: load regulation, 2: ground fault
Startup wait time | RW | 20091 | 4E7B | s | [10-900][60]
Fault recovery time | RW | 20092 | 4E7C | s | [0-3600][60]
Grid pickup total power compensation | RW | 20118 | 4E96 | kWh | 32-bit data, can be positive or negative, value 10 means 1kWh, value 1 means 0.1kWh
|  | 20119 | 4E97
Grid feeder total power compensation | RW | 20120 | 4E98
|  | 20121 | 4E99
DRM enable | RW | 20113 | 4E91 | / | 0xAA-enable; 0x55-disable [0x55]
Photovoltaic installation power | RW | 21225 | 52E9 | kW | A value of 1 means 0.1kW
Other power generation system power | RW | 21224 | 52E8 | kW | A value of 1 means 0.1kW
Off-grid enablement setting | RW | 23000 | 59D8 | / | 0xAA-enable; 0x55-disable
MPPT mode | RW | 20206 | 4EEE | / | 0: no PV, 0x55: independent, 0xAA: parallel [0x55]

## 2.功率调节参数
| Parameter Name | Read Write | Address (DEC) | Address (HEX) | Unit | Description
Active Regulation | Active slow start enable after fault | RW | 21196 | 52CC | / | 0xAA-enable; 0x55-off [0xAA]
| Active slow start time after fault | RW | 21197 | 52CD | s | [1-1200][600]
| Active speed control enable | RW | 21200 | 52D0 | / | 0xAA-enable; 0x55-off [0xAA]
| Active power falling speed | RW | 21201 | 52D1 | %/min | [1-6000][16], power change per minute, default 16 means power change per minute 16% of rated power
| Active power rising speed | RW | 21202 | 52D2 | %/min | [1-6000][16]
| Active regulation power-down save switch | RW | 21203 | 52D3 | / | 0xAA-enable; 0x55-off [0x55]
| Power limit switch | RW | 21204 | 52D4 | / | 0xAA-enable; 0x55-off [0xAA]
| Power limit percentage setting | RW | 21205 | 52D5 | % | [0-1000][1000], 1000 means 100%
Feeder power limitation | Feeder power limit enable | RW | 21221 | 52E5 | / | 0x55-Off [0x55], 0xA1: Soft Limit, 0xA2: Hard Limit, 0xA3: Generation Limit
| Feeder limit value percentage | RW | 21223 | 52E7 | % | [0-1000][1000], 1000 means 100%
Reactive power regulation | Reactive regulation power-down save switch | RW | 21604 | 5464 | / | 0xAA-enable; 0x55-off [0xAA]
| Reactive power regulation mode selection | RW | 21605 | 5465 | / | 0x55-off; 0xA1-power factor setting enabled; 0xA5: reactive power direct feed mode
| Reactive power percentage setting | RW | 21606 | 5466 | / | [-1000 - 1000][0]
| Power factor setting | RW | 21608 | 5468 | / | [-1000 - -800]; [800 - 1000][1000]
| Reactive power setting | RW | 21618 | 5472 | VA | [-6000 ~ 6000], 1 means 1VA
Voltage detection before grid connection | Grid detection switch before grid connection | RW | 22535 | 5807 | / | 0xAA-enable; 0x55- disable [0xAA]
| Lower grid frequency limit | RW | 22536 | 5808 | Hz | [4700 - 4998] [4750]
| Grid frequency upper limit | RW | 22537 | 5809 | Hz | [5002-5200][5015]
| Grid voltage lower limit | RW | 22549 | 5815 | % | [500 -1000][891]
| Upper grid voltage limit | RW | 22550 | 5816 | % | [1000-1400][1100]
| Grid detection time | RW | 22551 | 5817 | s | [10-900][60],1 means 1s
| Grid-connected active rising speed | RW | 22552 | 5818 |  | [3-6000][16].

## 3.能量管理参数
| Parameter Name | Read Write | Address (DEC) | Address (HEX) | Unit | Description
General Commands | Energy Management Mode | RW | 23146 | 5A6A | / | 0: self-generated, 2: forced charging and discharging
| Battery Charge and Discharge Commands | RW | 23147 | 5A6B | / | 0xAA: charging, 0xBB: discharging, 0xCC: no action [0xCC]
| Battery Charge and Discharge Power | RW | 23148 | 5A6C | kW | A value of 100 represents 1kW [0]
Battery Discharge Parameters | Weekday Discharge Start Time 1-Hour | RW | 23151 | 5A6F | h | [0-23][0]
| Weekday discharge start time 1-minute | RW | 23152 | 5A70 | min | [0-59][0]
| Weekday discharge end time 1-hour | RW | 23153 | 5A71 | h | [0-24][24]
| Weekday discharge end time 1-minute | RW | 23154 | 5A72 | min | [0-59][0]
| Weekday Discharge Start Time 2-Hour | RW | 23155 | 5A73 | h | [0-23][0]
| Weekday Discharge Start Time 2-Minutes | RW | 23156 | 5A74 | min | [0-59][0]
| Weekday Discharge End Time 2-Hour | RW | 23157 | 5A75 | h | [0-24][24]
| Weekday discharge end time 2-minute | RW | 23158 | 5A76 | min | [0-59][0]
| Non-working day discharge enable | RW | 23179 | 5A8B | / | 0xAA-enable; 0x55-disable [0xAA]
| Non-Workday Discharge Start Time 1-Hour | RW | 23180 | 5A8C | h | [0-23][0]
| Non-working day discharge start time 1-minute | RW | 23181 | 5A8D | min | [0-59][0]
| Non-Workday Discharge End Time 1-Hour | RW | 23182 | 5A8E | h | [0-24][24]
| Non-working day discharge end time 1-minute | RW | 23183 | 5A8F | min | [0-59][0]
| Non-Workday Discharge Start Time 2-Hour | RW | 23184 | 5A90 | h | [0-23][0]
| Non-Working Day Discharge Start Time 2-Minutes | RW | 23185 | 5A91 | min | [0-59][0]
| Non-Working Day Discharge End Time 2-Hour | RW | 23186 | 5A92 | h | [0-24][24]
| Non-Workday Discharge End Time 2-Minutes | RW | 23187 | 5A93 | min | [0-59][0]
Battery Forced Charge Parameters | Energy Management Forced Charge Enable | RW | 23208 | 5AA8 | / | 0xAA-enable; 0x55-disable [0x55]
| Energy Management Force Charge All Days Selection | RW | 23209 | 5AA9 | / | [0-1][1], 1 means that all days determine whether to charge or not, and 0 determines whether to charge or not only at normal times
| Energy Management Forced Charge Start Time 1-Hour | RW | 23210 | 5AAA | h | [0-23][0]
| Energy Management Forced Charge Start Time 1-minute | RW | 23211 | 5AAB | min | [0-59][0]
| Energy Management Forced Charge End Time 1-Hour | RW | 23212 | 5AAC | h | [0-24][0]
| Energy Management Forced Charge End Time 1-minute | RW | 23213 | 5AAD | min | [0-59][0]
| Forced Charge Target SOC1 | RW | 23214 | 5AAE | % | [0-100][0]，100means100%
| Energy Management Forced Charge Start Time 2-Hour | RW | 23215 | 5AAF | h | [0-23][0]
| Energy Management Forced Charge Start Time 2-minutes | RW | 23216 | 5AB0 | min | [0-59][0]
| Energy Management Forced Charge End Time 2-Hour | RW | 23217 | 5AB1 | h | [0-24][0]
| Energy Management Forced Charge End Time 2-minute | RW | 23218 | 5AB2 | min | [0-59][0]
| Forced charging target SOC2 | RW | 23219 | 5AB3 | % | [0-100][0]，100means100%
SOC | Maximum SOC | RW | 23031 | 59F7 | % | [500-1000][1000] 1000means 100.0%
| Minimum SOC | RW | 23032 | 59F8 | % | [0-500][0], 500means 50.0%

## 4.电池参数
Parameter Name | Read/Write Characteristics | Address (DEC) | Address (HEX) | Unit | Description
Maximum SOC | RW | 23031 | 59F7 | % | [500-1000][1000]，1000means100.0%
Minimum SOC | RW | 23032 | 59F8 | % | [0-500][0]，500means50.0%

## 5.通讯参数
Parameter Name | Read/Write Characteristics | Address (DEC) | Address (HEX) | Unit | Description
Modbus address | RW | 20460 | 4FEC | / | [1-246][1]

## Monitoring
| Parameter Name | Read Write | Address (DEC) | Address (HEX) | Unit | Description
Electricity Generation | PV1 Voltage | R | 4061 | 0FDD | V | 1=0.1V
| PV1 Current | R | 4062 | 0FDE | A | 1=0.1A
| PV1 Power |  |  |  |  | N/A
| PV2 Voltage | R | 4063 | 0FDF
| PV2 Current | R | 4064 | 0FE0
| PV2 Power |  |  |  |  | N/A
| PV total power | R | 4067 | 0FE3 | W | 32 bits
|  |  | 4068 | 0FE4
| Daily PV Power Generation | R | 10002 | 2712 | kWh | 1=0.1kWh
| Total PV Production | R | 10003 | 2713 | kWh | 32 bits 1=0.1kWh
|  |  | 10004 | 2714
| L1 Voltage | R | 4069 | 0FE5 | V | 1=0.1V
| L2 Voltage | R | 4070 | 0FE6 | V | 1=0.1V
| L3 Voltage | R | 4071 | 0FE7 | V | 1=0.1V
| L1 Current | R | 4072 | 0FE8 | A | 1=0.1A
| L2 Current | R | 4073 | 0FE9 | A | 1=0.1A
| L3 Current | R | 4074 | 0FEA | A | 1=0.1A
| Total AC Output Power | R | 4081 | 0FF1 | W | 32 bits
|  |  | 4082 | 0FF2
| Reactive Power | R | 4083 | 0FF3 | W | 32 bits
|  |  | 4084 | 0FF4
| Total AC Apparent Power | R | 4059 | 0FDB | W | 32 bits
|  |  | 4060 | 0FDC
| Power factor value | R | 4085 | 0FF5 |  | Signed 16 bits
| Real-time feeder power | R | 5401 | 1519 | W
Power Grid Electricity Consumption | Grid Frequency | R | 4198 | 1066 | Hz | 1=0.01Hz
| Daily Grid Feed-in | R | 10045 | 273D | kWh | 1=0.1kWh
| AC cumulative output power | R |  |  |  | N/A
| Cumulative Grid Feed-in | R | 10046 | 273E | kWh | 32 bits 1=0.1kWh
|  |  | 10047 | 273F
| Daily Energy Purchased | R | 10036 | 2734 | kWh | 1=0.1kWh
| Cumulative Energy Purchased | R | 10037 | 2735 | kWh | 32 bits 1=0.1kWh
|  |  | 10038 | 2736
| AC daily output power | R |  |  |  | N/A
| Total Consumption Power | R | 10008 |  | W
Battery | Battery Voltage | R | 10020 | 2724 | V | 1=0.1V
| Battery Current | R | 10021 | 2725 | A | 1=0.1A
| Battery Power | R | 10022 | 2726 | W | Signed 16 bits
| Battery Capacity | R |  |  |  | N/A
| SoC | R | 10023 | 2727 | %
| SoH | R | 10024 | 2728 | %
| Total Charging Energy | R | 10041 | 2739 | kWh | 32 bits 1=0.1kWh
|  |  | 10042 | 273A
| Total Discharging Energy | R | 10027 | 272B | kWh | 32 bits 1=0.1kWh
|  |  | 10028 | 272C
| Daily Charging Energy | R | 10040 | 2738 | kWh | 1=0.1kWh
| Daily Discharging Energy | R | 10026 | 272A | kWh | 1=0.1kWh
| PV daily charging capacity | R |  |  |  | N/A
| PV Total charge capacity | R |  |  |  | N/A
| Temperature Battery | R | 10025 |  | °C
| Internal Temperature | R | 4058 |  | °C | 16bits signed 1=0.1°C
Other & State | Busbar Voltage 1 | R | 4197 | 1065 | V | 1=0.1V
| energy flow state | R |  |  |  | N/A
| PV daily self-generated self- consumption | R |  |  |  | N/A
| PV total self-generated self-consumption | R |  |  |  | N/A
| Daily spontaneous self-use rate | R | 10129 |  | %
| Limited power mode: | R | 10130
| Arc self-test result | R | 5759
| Power limit switch | R | 21204 | 52D4 | / | 0xAA-enable; 0x55-off [0xAA]
| Power limit value | R | 21205 | 52D5 | % | [0-1000][1000], 1000 means 100%
| Power Company ID | R |  |  |  | N/A
| Grid Standard ID | R |  |  |  | N/A
| MPPT mode | R | 20206
| Grid connection type selection | R |  |  |  | N/A
| Insulation resistance | R | 4121 |  | kΩ
| Inverter status | R | 10000 | 2710 |  | 0x0000 Grid-connected normal operation 0x0800 Forced grid-connected operation 0x1000 off-grid operation 0x1200 Initial standby 0x1400 IDLE 0x1600 Starting (self-test) 0x4001 Emergency charging operation
| Energy Management Mode | R | 23146 |  |  | 0: Self-used Mode 2: Forced charging & discharging mode
| On/Off Status | R | 4056
| Current Country | R | 22310 | 5726
| Load Mode | R | 23000 | 59D8
| DRM status | R